{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":45,"n_cols":6,"rows_kept":45,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","BSV4Q-PV"]
[]
[]
[]
[]
["","","","","","BSV4Q100PV1"]
["Standard Accessories","Installation manual","","","","Installation manual"]
["","Attached piping","","","","Attached piping"]
["","Insulation pipe cover","","","","Insulation pipe cover"]
["","Clamps","","","","Clamps"]
["Maximum number of connectable indoor units per branch","","","","","6"]
["Maximum number of connectable indoor units","","","","","24"]
["Piping connections","Outdoor unit","Liquid","Type","","Brazing connection"]
["","","","OD","mm","12.7"]
["","","Discharge gas","Type","","Brazing connection"]
["","","","OD","mm","19.1"]
["","","Gas","Type","","Brazing connection"]
["","","","OD","mm","28.6"]
["","Indoor unit","Gas","Type","","Brazing connection"]
["","","","OD","mm","15.9"]
["","","Liquid","OD","mm","9.5"]
["","","","Type","","Brazing connection"]
["Power input","Cooling","","Nom.","kW","0.020"]
["","Heating","","Nom.","kW","0.020"]
["Maximum capacity index of connectable indoor units per branch","","","","","100"]
["Dimensions","Unit","","Width","mm","1,053"]
["","","","Depth","mm","635"]
["","","","Height","mm","209"]
["Weight","Unit","","","kg","60"]
["Number of branches","","","","","4"]
["Maximum capacity index of connectable indoor units","","","","","400"]
["Power supply","Phase","","","","1~"]
["","Frequency","","","Hz","50"]
["","Voltage","","","V","220-240"]
["","Name","","","","V1"]
["Notes","","","","","(1) - In case of connection with a 20~50 type indoor unit, match to the size of the field pipe using the attached pipe. Connection between the attached pipe and the field pipe must be brazed."]
["","","","","","(2) - In case the joint diameter does not fit on the triple piping side, a reducer is needed (field supply)"]
["","","","","","(3) - Insulators are necessary (field supply) for the triple piping side"]
["","","","","","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(5) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(6) - MCA/MFA: MCA = 1.25 x FLA"]
["","","","","","(7) - MFA ≤ 4 x FLA"]
["","","","","","(8) - Next lower standard fuse rating minimum 15A"]
["","","","","","(9) - Select wire size based on the value of MCA"]
["","","","","","(10) - Instead of a fuse, use a circuit breaker"]