{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":55,"n_cols":8,"rows_kept":55,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","ERA-AY"]
[]
[]
[]
[]
["","","","","","ERA100A7Y1B","ERA125A7Y1B","ERA140A7Y1B"]
["Cooling capacity","Nom.","","35°CDB","kW","12.1 (1)","14","15.5 (1)"]
["Heating capacity","Nom.","","6°CWB","kW","12.1 (2)","14","15.5 (2)"]
["SEER","","","","","7.9 (3)","7.4 (3)","7.3 (3)"]
["SCOP","","","","","4.9 (3)","4.5 (3)","4.5 (3)"]
["Indoor index connection","Min.","","","","63","100","100"]
["","Max.","","","","100","125","140"]
["Dimensions","Unit","","Height","mm","869","869","869"]
["","","","Width","mm","1100","1100","1100"]
["","","","Depth","mm","460","460","460"]
["Weight","Unit","","","kg","102","102","102"]
["Fan","External static pressure","","Max.","Pa","45","45","45"]
["Compressor","Type","","","","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor"]
["Operation range","Cooling","","Min.","°CDB","-5","-5","-5"]
["","","","Max.","°CDB","46","46","46"]
["","Heating","","Min.","°CWB","-20","-20","-20"]
["","","","Max.","°CWB","15.5","15.5","15.5"]
["Sound power level","Cooling","","Nom.","dBA","67","68.1 (4)","69"]
["Sound pressure level","Cooling","","Nom.","dBA","49","51","51"]
["Refrigerant","Type","","","","R-32","R-32","R-32"]
["","GWP","","","","675","675","675"]
["","Charge","","","tCO2Eq","2.3","2.3","2.3"]
["","Charge","","","kg","3.4","3.4","3.4"]
["Piping connections","Liquid","","Type","","Braze connection","Braze connection","Braze connection"]
["","","","OD","mm","9.52","9.52","9.52"]
["","Gas","","Type","","Braze connection","Braze connection","Braze connection"]
["","","","OD","mm","15.9","15.9","15.9"]
["","Total piping length","System","Actual","m","50 (6)","50 (6)","50 (6)"]
["","Level difference","OU - IU","Outdoor unit in highest position","m","50","50","50"]
["","","","Indoor unit in highest position","m","40","40","40"]
["Standard Accessories","Auxiliary piping set","","","","1","1","1"]
["","Installation and operation manual","","","","1","1","1"]
["Power supply","Name","","","","Y1","Y1","Y1"]
["","Phase","","","","3N~","3N~","3N~"]
["","Frequency","","","Hz","50","50","50"]
["","Voltage","","","V","380-415","380-415","380-415"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m"]
["","","","","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m"]
["","","","","","(3) - Defined for a system capacity ratio of 100% ± 5%, configured for complete air recirculation applications.","(3) - Defined for a system capacity ratio of 100% ± 5%, configured for complete air recirculation applications.","(3) - Defined for a system capacity ratio of 100% ± 5%, configured for complete air recirculation applications."]
["","","","","","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates."]
["","","","","","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings."]
["","","","","","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual"]
["","","","","","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB"]
["","","","","","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current."]
["","","","","","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current."]
["","","","","","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","","(11) - TOCA means the total value of each OC set.","(11) - TOCA means the total value of each OC set.","(11) - TOCA means the total value of each OC set."]
["","","","","","(12) - FLA means the nominal running current of the fan","(12) - FLA means the nominal running current of the fan","(12) - FLA means the nominal running current of the fan"]
["","","","","","(13) - For AHU HEX volume limitations, refer to the engineering data book or installation manual","(13) - For AHU HEX volume limitations, refer to the engineering data book or installation manual","(13) - For AHU HEX volume limitations, refer to the engineering data book or installation manual"]
["","","","","","(14) - For detailed contents of standard accessories, see installation/operation manual","(14) - For detailed contents of standard accessories, see installation/operation manual","(14) - For detailed contents of standard accessories, see installation/operation manual"]