{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":66,"n_cols":25,"rows_kept":66,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAD-TZSRB"]
[]
[]
[]
[]
["","","","","","EWAD160TZSRB1","EWAD190TZSRB1","EWAD240TZSRB1","EWAD270TZSRB1","EWAD300TZSRB1","EWAD360TZSRB1","EWAD380TZSRB2","EWAD455TZSRB2","EWAD500TZSRB2","EWAD570TZSRB2","EWAD610TZSRB2","EWAD660TZSRB2","EWAD700TZSRB2","EWAD820TZSRB2","EWAD900TZSRB2","EWAD990TZSRB2","EWADC10TZSRB2","EWADC11TZSRB2","EWAD450TZSRB2 (Archived)","EWAD495TZSRB2 (Archived)"]
["Cooling capacity","Nom.","","","kW","169.1","200.9","235.3","268.8","306","351.4","394","454.6","499.1","568.6","610.4","659","699.9","800","895","956","1,013","1,067","454.6","499.1"]
["Capacity control","Method","","","","","","","","","","","Variable","Variable"]
["","Minimum capacity","","","%","37","31","34","29","25","24","16","17","16","14","13","12","12","10","10","10","10","10","17","16"]
["Power input","Cooling","","Nom.","kW","56.48","69.9","82.99","89.94","108.6","118","140.2","164.8","175.4","199.1","218.4","240.3","250.3","247.8","294.1","316","335.6","358.9","164.8","175.4"]
["EER","","","","","2.995","2.874","2.835","2.989","2.817","2.954","2.81","2.759","2.846","2.856","2.795","2.742","2.796","3.229","3.043","3.016","3.018","2.973","2.759","2.846"]
["IPLV","","","","","5.3","5.27","5.04","5.19","5.37","5.53","5.3","5.26","5.43","5.6","5.61","5.6","5.67","5.92","5.74","5.77","5.75","5.86","5.26","5.43"]
["SEER","","","","","4.28","4.39","4.31","4.46","4.5","4.65","4.38","4.63","4.64","4.56","4.79","4.62","4.69","5.45","5.41","5.42","5.48","5.52","4.34","4.43"]
["Dimensions","Unit","","Depth","mm","2,283","2,283","2,283","3,183","3,183","4,083","4,083","4,083","4,983","5,883","5,883","5,883","6,783","7,783","7,783","8,820","9,591","10,461","4,083","4,983"]
["","","","Height","mm","2,483","2,483","2,483","2,483","2,483","2,483","2,483","2,483","2,483","2,483","2,483","2,483","2,483","2,482","2,482","2,482","2,482","2,482","2,483","2,483"]
["","","","Width","mm","2,258","2,258","2,258","2,258","2,258","2,258","2,258","2,258","2,258","2,258","2,258","2,258","2,258","2,258","2,258","2,258","2,258","2,258","2,258","2,258"]
["Weight","Operation weight","","","kg","2,186","2,217","2,287","2,501","2,560","2,921","4,402","4,424","4,675","4,961","5,250","5,259","5,529","7,247","7,347","7,702","7,980","8,273","4,424","4,675"]
["","Unit","","","kg","2,166","2,191","2,249","2,475","2,522","2,871","4,244","4,260","4,517","4,803","4,980","5,004","5,274","6,997","7,097","7,452","7,730","8,023","4,260","4,517"]
["Casing","Colour","","","","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white"]
["","Material","","","","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet"]
["Air heat exchanger","Type","","","","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel"]
["Fan","Quantity","","","","4","4","4","6","6","8","8","8","10","12","12","12","14","16","16","18","20","22","8","10"]
["","Type","","","","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller"]
["Fan motor","Drive","","","","ON/OFF","ON/OFF","ON/OFF","ON/OFF","ON/OFF","ON/OFF","ON/OFF","ON/OFF","ON/OFF","ON/OFF","ON/OFF","ON/OFF","ON/OFF","ON/OFF","ON/OFF","ON/OFF","ON/OFF","ON/OFF","ON/OFF","ON/OFF"]
["Compressor","Quantity","","","","1","1","1","1","1","1","2","2","2","2","2","2","2","2","2","2","2","2","2","2"]
["","Type","","","","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Driven vapour compression","Driven vapour compression"]
["","Starting method","","","","Inverter driven","Inverter driven","Inverter driven","Inverter driven","Inverter driven","Inverter driven","Inverter driven","Inverter driven","Inverter driven","Inverter driven","Inverter driven","Inverter driven","Inverter driven","Inverter driven","Inverter driven","Inverter driven","Inverter driven","Inverter driven","Inverter driven","Inverter driven"]
["Operation range","Air side","Cooling","Min.","°CDB","-18","-18","-18","-18","-18","-18","-18","-18","-18","-18","-18","-18","-18","-18","-18","-18","-18","-18","-18","-18"]
["","","","Max.","°CDB","47","47","47","47","47","47","47","47","47","47","47","47","47","45","45","45","45","45","47","47"]
["","Water side","Evaporator","Min.","°CDB","-8","-8","-8","-8","-8","-8","-8","-8","-8","-8","-8","-8","-8","-15","-15","-15","-15","-15","-8","-8"]
["","","","Max.","°CDB","18","18","18","18","18","18","18","18","18","18","18","18","18","20","20","20","20","20","18","18"]
["Sound power level","Cooling","","Nom.","dBA","86","87","87","88","88","90","90","90","90","91","91","92","94","94","94","95","95","95","90","90"]
["Sound pressure level","Cooling","","Nom.","dBA","67","68","68","68","69","70","70","70","70","70","70","71","73","73","73","73","73","73","70","70"]
["Refrigerant","Type","","","","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a"]
["","GWP","","","","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430"]
["","Charge","","","kg","27","29","33","38","41","52","58","59","68","75","77","83","90","104","104","117","130","143","59","68"]
["","Circuits","","Quantity","","1","1","1","1","1","1","2","2","2","2","2","2","2","2","2","2","2","2","2","2"]
["Piping connections","Evaporator water inlet/outlet (OD)","","","","3\"","3\"","4\"","4\"","4\"","4\"","5\"","5\"","5\"","5\"","6”","6”","6”","168.3 mm","219.1mm","219.1mm","219.1mm","219.1mm","5\"","5\""]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400"]
["","Voltage range","","Min.","%","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","","","Max.","%","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10"]
["Unit","Starting current","","Max","A","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["","Running current","Cooling","Nom.","A","102","123","188","177","188","200","247","374","368","363","378","398","416","422","496","530","561","599","374","368"]
["","","","Max","A","130","149","160","187","220","246","298","320","350","374","439","466","486","523","585","635","688","745","320","350"]
["","Max unit current for wires sizing","","","A","141","156","174","187","239","247","313","349","368","374","479","483","488","568","637","692","750","813","349","368"]
["Notes","","","","","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0"]
["","","","","","(2) - The value refers to the pressure drop in the evaporator only","(2) - The value refers to the pressure drop in the evaporator only","(2) - The value refers to the pressure drop in the evaporator only","(2) - The value refers to the pressure drop in the evaporator only","(2) - The value refers to the pressure drop in the evaporator only","(2) - The value refers to the pressure drop in the evaporator only","(2) - The value refers to the pressure drop in the evaporator only","(2) - The value refers to the pressure drop in the evaporator only","(2) - The value refers to the pressure drop in the evaporator only","(2) - The value refers to the pressure drop in the evaporator only","(2) - The value refers to the pressure drop in the evaporator only","(2) - The value refers to the pressure drop in the evaporator only","(2) - The value refers to the pressure drop in the evaporator only","(2) - The value refers to the pressure drop in the evaporator only","(2) - The value refers to the pressure drop in the evaporator only","(2) - The value refers to the pressure drop in the evaporator only","(2) - The value refers to the pressure drop in the evaporator only","(2) - The value refers to the pressure drop in the evaporator only","(2) - The value refers to the pressure drop in the evaporator only","(2) - The value refers to the pressure drop in the evaporator only"]
["","","","","","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1"]
["","","","","","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit."]
["","","","","","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition"]
["","","","","","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request."]
["","","","","","(7) - All data refers to the standard unit without options.","(7) - All data refers to the standard unit without options.","(7) - All data refers to the standard unit without options.","(7) - All data refers to the standard unit without options.","(7) - All data refers to the standard unit without options.","(7) - All data refers to the standard unit without options.","(7) - All data refers to the standard unit without options.","(7) - All data refers to the standard unit without options.","(7) - All data refers to the standard unit without options.","(7) - All data refers to the standard unit without options.","(7) - All data refers to the standard unit without options.","(7) - All data refers to the standard unit without options.","(7) - All data refers to the standard unit without options.","(7) - All data refers to the standard unit without options.","(7) - All data refers to the standard unit without options.","(7) - All data refers to the standard unit without options.","(7) - All data refers to the standard unit without options.","(7) - All data refers to the standard unit without options.","(7) - All data refers to the standard unit without options.","(7) - All data refers to the standard unit without options."]
["","","","","","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%."]
["","","","","","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced."]
["","","","","","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current."]
["","","","","","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current"]
["","","","","","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage."]
["","","","","","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1"]
["","","","","","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book"]
["","","","","","(15) - All data are subject to change without notice. Please refer to the unit nameplate data.","(15) - All data are subject to change without notice. Please refer to the unit nameplate data.","(15) - All data are subject to change without notice. Please refer to the unit nameplate data.","(15) - All data are subject to change without notice. Please refer to the unit nameplate data.","(15) - All data are subject to change without notice. Please refer to the unit nameplate data.","(15) - All data are subject to change without notice. Please refer to the unit nameplate data.","(15) - All data are subject to change without notice. Please refer to the unit nameplate data.","(15) - All data are subject to change without notice. Please refer to the unit nameplate data.","(15) - All data are subject to change without notice. Please refer to the unit nameplate data.","(15) - All data are subject to change without notice. Please refer to the unit nameplate data.","(15) - All data are subject to change without notice. Please refer to the unit nameplate data.","(15) - All data are subject to change without notice. Please refer to the unit nameplate data.","(15) - All data are subject to change without notice. Please refer to the unit nameplate data.","(15) - All data are subject to change without notice. Please refer to the unit nameplate data.","(15) - All data are subject to change without notice. Please refer to the unit nameplate data.","(15) - All data are subject to change without notice. Please refer to the unit nameplate data.","(15) - All data are subject to change without notice. Please refer to the unit nameplate data.","(15) - All data are subject to change without notice. Please refer to the unit nameplate data.","(15) - All data are subject to change without notice. Please refer to the unit nameplate data.","(15) - All data are subject to change without notice. Please refer to the unit nameplate data."]
["","","","","","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS)."]
["","","","","","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding"]
["","","","","","(18) - Fluid: Water","(18) - Fluid: Water","(18) - Fluid: Water","(18) - Fluid: Water","(18) - Fluid: Water","(18) - Fluid: Water","(18) - Fluid: Water","(18) - Fluid: Water","(18) - Fluid: Water","(18) - Fluid: Water","(18) - Fluid: Water","(18) - Fluid: Water","(18) - Fluid: Water","(18) - Fluid: Water","(18) - Fluid: Water","(18) - Fluid: Water","(18) - Fluid: Water","(18) - Fluid: Water","(18) - Fluid: Water","(18) - Fluid: Water"]
["","","","","","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels."]