{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":62,"n_cols":8,"rows_kept":62,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAQ-ACW1"]
[]
[]
[]
[]
["","","","","","EWAQ009ACW1","EWAQ011ACW1","EWAQ013ACW1"]
["Sound pressure level","Cooling","","Nom.","dBA","51 (6)","51 (6)","52 (6)"]
["","Night quiet mode","","Cooling","dBA","45","45","46"]
["Hydraulic components","Expansion vessel","","Volume","l","10","10","10"]
["Operation range","Air side","Cooling","Min.","°CDB","10","10","10"]
["","","","Max.","°CDB","46","46","46"]
["","Water side","Cooling","Max.","°CDB","20","20","20"]
["","","","Min.","°CDB","5","5","5"]
["Refrigerant charge","Per circuit","","","kg","2.95","2.95","2.95"]
["","Refrigerant charge-=-Per circuit-=-TCO2Eq","","","TCO2Eq","6.16","6.16","6.16"]
["Compressor","Type","","","","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor"]
["","Starting method","","","","Inverter driven","Inverter driven","Inverter driven"]
["","Quantity","","","","1","1","1"]
["Weight","Unit","","","kg","168","168","168"]
["Air heat exchanger","Type","","","","Hi-XSS (8)","Hi-XSS (8)","Hi-XSS (8)"]
["EER","","","","","4.19 (2), 2.99 (3)","3.79 (2), 2.85 (3)","3.08 (2), 2.57 (3)"]
["ESEER","","","","","4.43 (4)","4.44 (4)","4.36 (4)"]
["Refrigerant","GWP","","","","2,087.5","2,087.5","2,087.5"]
["","Type","","","","R-410A","R-410A","R-410A"]
["","Circuits","","Quantity","","1.00","1.00","1.00"]
["","Control","","","","Electronic expansion valve","Electronic expansion valve","Electronic expansion valve"]
["Fan motor","Speed","Cooling","Nom.","rpm","780","780","780"]
["Cooling capacity","Nom.","","","kW","12.9 (2), 9.10 (3)","15.7 (2), 11.1 (3)","17.0 (2), 13.3 (3)"]
["Water heat exchanger","Water volume","","","l","1.01","1.01","1.01"]
["","Type","","","","Brazed plate","Brazed plate","Brazed plate"]
["","Water flow rate","","Min.","l/min","16","16","16"]
["Power input","Cooling","","Nom.","kW","3.08 (2), 3.05 (3)","4.13 (2), 3.90 (3)","5.52 (2), 5.18 (3)"]
["Sound power level","Cooling","","Nom.","dBA","64 (6)","64 (6)","66 (6)"]
["Dimensions","Unit","","Width","mm","1,420","1,420","1,420"]
["","","","Depth","mm","382","382","382"]
["","","","Height","mm","1,435","1,435","1,435"]
["Capacity control","Method","","","","Variable (inverter)","Variable (inverter)","Variable (inverter)"]
["Fan","Air flow rate","Cooling","Nom.","m³/min","96.0","96.0","100"]
["Water circuit","Total water volume","","","l","4.00 (7)","4.00 (7)","4.00 (7)"]
["","Drain valve / fill valve","","","","Yes","Yes","Yes"]
["","Air purge valve","","","","Yes","Yes","Yes"]
["","Piping","","","inch","5/4\"","5/4\"","5/4\""]
["","Piping connections diameter","","","inch","G 5/4\" (female)","G 5/4\" (female)","G 5/4\" (female)"]
["","Minimum water volume in the system","","","l","20 (9)","20 (9)","20 (9)"]
["","Shut off valve","","","","Yes","Yes","Yes"]
["","Manometer","","","","Yes","Yes","Yes"]
["","Safety valve","","","bar","3","3","3"]
["Compressor","Starting method","","","","Inverter driven","Inverter driven","Inverter driven"]
["","Crankcase heater","","","W","33","33","33"]
["Power supply","Phase","","","","3N~","3N~","3N~"]
["","Name","","","","W1","W1","W1"]
["","Frequency","","","Hz","50","50","50"]
["","Voltage","","","V","400","400","400"]
["Notes","","","","","(1) - Tamb 35°C - LWE 7°C (DT=5°C)","(1) - Tamb 35°C - LWE 7°C (DT=5°C)","(1) - Tamb 35°C - LWE 7°C (DT=5°C)"]
["","","","","","(2) - Underfloor program: cooling Ta 35°C - LWE 18°C (Dt: 5°C); heating Ta DB/WB 7°C/6°C - LWC 35°C (Dt: 5°C)","(2) - Underfloor program: cooling Ta 35°C - LWE 18°C (Dt: 5°C); heating Ta DB/WB 7°C/6°C - LWC 35°C (Dt: 5°C)","(2) - Underfloor program: cooling Ta 35°C - LWE 18°C (Dt: 5°C); heating Ta DB/WB 7°C/6°C - LWC 35°C (Dt: 5°C)"]
["","","","","","(3) - Fan coil program: cooling Ta 35°C - LWE 7°C ( Dt: 5°C); heating Ta DB/WB 7°C/6°C - LWC 45°C ( Dt: 5°C )","(3) - Fan coil program: cooling Ta 35°C - LWE 7°C ( Dt: 5°C); heating Ta DB/WB 7°C/6°C - LWC 45°C ( Dt: 5°C )","(3) - Fan coil program: cooling Ta 35°C - LWE 7°C ( Dt: 5°C); heating Ta DB/WB 7°C/6°C - LWC 45°C ( Dt: 5°C )"]
["","","","","","(4) - All performance calculations are strictly according to Eurovent standard","(4) - All performance calculations are strictly according to Eurovent standard","(4) - All performance calculations are strictly according to Eurovent standard"]
["","","","","","(5) - For average climate and low temperature application","(5) - For average climate and low temperature application","(5) - For average climate and low temperature application"]
["","","","","","(6) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)","(6) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)","(6) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)"]
["","","","","","(7) - Including piping + PHE; excluding expansion vessel","(7) - Including piping + PHE; excluding expansion vessel","(7) - Including piping + PHE; excluding expansion vessel"]
["","","","","","(8) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information.","(8) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information.","(8) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information."]
["","","","","","(9) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info.","(9) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info.","(9) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info."]