{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":60,"n_cols":9,"rows_kept":60,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAQ-BVP"]
[]
[]
[]
[]
["","","","","","EWAQ004BAVP","EWAQ005BAVP","EWAQ006BAVP","EWAQ008BAVP"]
["Sound pressure level","Cooling","","Nom.","dBA","48 (11)","49 (11)","52 (10)","53 (10)"]
["","Night quiet mode","","Cooling","dBA","44 (11)","44 (11)","43 (10)","43 (10)"]
["Hydraulic components","Expansion vessel","","Volume","l","3","3","7","7"]
["Operation range","Air side","Cooling","Min.","°CDB","10","10","10","10"]
["","","","Max.","°CDB","43","43","46","46"]
["","Water side","Cooling","Max.","°CDB","22","22","22","22"]
["","","","Min.","°CDB","5","5","5","5"]
["Refrigerant charge","Per circuit","","","kg","2.10","2.10","2.70","2.70"]
["","Refrigerant charge-=-Per circuit-=-TCO2Eq","","","TCO2Eq","4.4","4.4","5.6","5.6"]
["Compressor","Type","","","","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor"]
["","Starting method","","","","Inverter driven","Inverter driven","Inverter driven","Inverter driven"]
["","Quantity","","","","1","1","1","1"]
["Weight","Unit","","","kg","83","83","106","106"]
["Air heat exchanger","Type","","","","Cross fin coil/Hi-X tubes and chromate coated waffle louvre fins","Cross fin coil/Hi-X tubes and chromate coated waffle louvre fins","Cross fin coil/Hi-X tubes and PE coated waffle louvre fins","Cross fin coil/Hi-X tubes and PE coated waffle louvre fins"]
["EER","","","","","3.14 (1), 4.80 (2)","3.06 (1), 4.51 (2)","3.15 (1), 5.35 (2)","3.10 (1), 4.99 (2)"]
["ESEER","","","","","4.45 (5)","4.49 (5)","5.25 (5)","5.24 (5)"]
["Refrigerant","GWP","","","","2,088","2,088","2,087.5","2,087.5"]
["","Type","","","","R-410A","R-410A","R-410A","R-410A"]
["","Circuits","","Quantity","","1","1","1","1"]
["","Control","","","","Electronic expansion valve","Electronic expansion valve","Electronic expansion valve","Electronic expansion valve"]
["Cooling capacity","Nom.","","","kW","4.00 (1), 4.01 (2)","4.93 (1), 5.07 (2)","5.88 (1), 6.07 (2)","7.95 (1), 8.23 (2)"]
["Water heat exchanger","Water volume","","","l","1","1","2","2"]
["","Type","","","","Brazed plate","Brazed plate","Brazed plate","Brazed plate"]
["","Water flow rate","","Min.","l/min","11 (7)","11 (7)","13","13"]
["Power input","Cooling","","Nom.","kW","1.27 (1), 0.840 (2)","1.61 (1), 1.12 (2)","1.87 (1), 1.13 (2)","2.57 (1), 1.65 (2)"]
["Sound power level","Cooling","","Nom.","dBA","63 (1)","64 (1)","69 (1)","69 (1)"]
["Dimensions","Unit","","Width","mm","1,090","1,090","1,160","1,160"]
["","","","Depth","mm","350","350","380","380"]
["","","","Height","mm","735","735","997","997"]
["Capacity control","Method","","","","Variable (inverter)","Variable (inverter)","Variable (inverter)","Variable (inverter)"]
["Fan","Air flow rate","Cooling","Nom.","m³/min","53 (1)","53 (1)","72 (1)","72 (1)"]
["Water circuit","Drain valve / fill valve","","","","Yes","Yes","Yes","Yes"]
["","Air purge valve","","","","Yes (Manually)","Yes (Manually)","Yes (Manually)","Yes (Manually)"]
["","Piping connections diameter","","","inch","1\" MBSP","1\" MBSP","1\" MBSP","1\" MBSP"]
["","Minimum water volume in the system","","","l","20","20","20","20"]
["","Shut off valve","","","","Yes","Yes","Yes","Yes"]
["","Manometer","","","","No","No","No","No"]
["Power supply","Phase","","","","1N~","1N~","1N~","1N~"]
["","Frequency","","","Hz","50","50","50","50"]
["","Voltage","","","V","230","230","230","230"]
["Notes","","","","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C"]
["","","","","","(2) - Cooling: entering evaporator water temp. 23°C; leaving evaporator water temp. 18°C; ambient air temp. 35°C; standard: non-Eurovent","(2) - Cooling: entering evaporator water temp. 23°C; leaving evaporator water temp. 18°C; ambient air temp. 35°C; standard: non-Eurovent","(2) - Cooling: entering evaporator water temp. 23°C; leaving evaporator water temp. 18°C; ambient air temp. 35°C; standard: non-Eurovent","(2) - Cooling: entering evaporator water temp. 23°C; leaving evaporator water temp. 18°C; ambient air temp. 35°C; standard: non-Eurovent"]
["","","","","","(3) - Heating: entering condenser water temp. 40°C; leaving condenser water temp. 45°C; ambient air temp. 7°CDB, 6°CWB; standard: Eurovent","(3) - Heating: entering condenser water temp. 40°C; leaving condenser water temp. 45°C; ambient air temp. 7°CDB, 6°CWB; standard: Eurovent","(3) - Heating: entering condenser water temp. 40°C; leaving condenser water temp. 45°C; ambient air temp. 7°CDB, 6°CWB; standard: Eurovent","(3) - Heating: entering condenser water temp. 40°C; leaving condenser water temp. 45°C; ambient air temp. 7°CDB, 6°CWB; standard: Eurovent"]
["","","","","","(4) - Heating: entering condenser water temp. 30°C; leaving condenser water temp. 35°C; ambient air temp. 7°CDB, 6°CWB; standard: Eurovent","(4) - Heating: entering condenser water temp. 30°C; leaving condenser water temp. 35°C; ambient air temp. 7°CDB, 6°CWB; standard: Eurovent","(4) - Heating: entering condenser water temp. 30°C; leaving condenser water temp. 35°C; ambient air temp. 7°CDB, 6°CWB; standard: Eurovent","(4) - Heating: entering condenser water temp. 30°C; leaving condenser water temp. 35°C; ambient air temp. 7°CDB, 6°CWB; standard: Eurovent"]
["","","","","","(5) - All performance calculations are strictly according to Eurovent standard","(5) - All performance calculations are strictly according to Eurovent standard","(5) - All performance calculations are strictly according to Eurovent standard","(5) - All performance calculations are strictly according to Eurovent standard"]
["","","","","","(6) - For average climate and low temperature application","(6) - For average climate and low temperature application","(6) - For average climate and low temperature application","(6) - For average climate and low temperature application"]
["","","","","","(7) - In case of flow medium brine, a minimal flow of 12 L/min is required","(7) - In case of flow medium brine, a minimal flow of 12 L/min is required","(7) - Operation area is extended to lower flow rates only in case the unit operates with heat pump only. (Not in startup, no BUH operation, no defrost operation).","(7) - Operation area is extended to lower flow rates only in case the unit operates with heat pump only. (Not in startup, no BUH operation, no defrost operation)."]
["","","","","","(8) - Operation area is extended to lower flow rates only in case the unit operates with heat pump only. (Not in startup, no BUH operation, no defrost operation).","(8) - Operation area is extended to lower flow rates only in case the unit operates with heat pump only. (Not in startup, no BUH operation, no defrost operation).","(8) - Including piping + PHE; excluding expansion vessel","(8) - Including piping + PHE; excluding expansion vessel"]
["","","","","","(9) - Including piping + PHE; excluding expansion vessel","(9) - Including piping + PHE; excluding expansion vessel","(9) - Lower if back-up heater is installed; In case of no back-up heater, then heat pump operation starts at 10°C","(9) - Lower if back-up heater is installed; In case of no back-up heater, then heat pump operation starts at 10°C"]
["","","","","","(10) - Lower if back-up heater is installed; In case of no back-up heater, then heat pump operation starts at 10°C","(10) - Lower if back-up heater is installed; In case of no back-up heater, then heat pump operation starts at 10°C","(10) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information.","(10) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information."]
["","","","","","(11) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information.","(11) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information.","(11) - Assembly ≤ category I: excluded from 2014/68/EU due to article 1, 2f","(11) - Assembly ≤ category I: excluded from 2014/68/EU due to article 1, 2f"]
["","","","","","(12) - Assembly ≤ category I: excluded from 2014/68/EU due to article 1, 2f","(12) - Assembly ≤ category I: excluded from 2014/68/EU due to article 1, 2f","(12) - Inverter controlled compressor starting current always <= max. running current","(12) - Inverter controlled compressor starting current always <= max. running current"]
["","","","","","(13) - Inverter controlled compressor starting current always <= max. running current","(13) - Inverter controlled compressor starting current always <= max. running current","(13) - Ssc: Short-circuit power","(13) - Ssc: Short-circuit power"]
["","","","","","","","(14) - European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current larger than 16A and ≤ 75A per phase.","(14) - European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current larger than 16A and ≤ 75A per phase."]