{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":50,"n_cols":19,"rows_kept":50,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAQ-F-XR"]
[]
[]
[]
[]
["","","","","","EWAQ170F-XR (Archived)","EWAQ190F-XR (Archived)","EWAQ210F-XR (Archived)","EWAQ240F-XR (Archived)","EWAQ300F-XR (Archived)","EWAQ310F-XR (Archived)","EWAQ330F-XR (Archived)","EWAQ340F-XR (Archived)","EWAQ390F-XR (Archived)","EWAQ410F-XR (Archived)","EWAQ430F-XR (Archived)","EWAQ500F-XR (Archived)","EWAQ580F-XR (Archived)","EWAQ650F-XR (Archived)"]
["Sound pressure level","Cooling","","Nom.","dBA","64","65","66","67","67","68","67","68","69","70","70","69","70","71"]
["Operation range","Air side","Cooling","Min.","°CDB","-18","-18","-18","-18","-18","-18","-18","-18","-18","-18","-18","-18","-18","-18"]
["","","","Max.","°CDB","52","52","52","52","52","52","52","52","52","52","52","52","52","52"]
["","Water side","Cooling","Max.","°CDB","18","18","18","18","18","18","18","18","18","18","18","18","18","18"]
["","","","Min.","°CDB","-13","-13","-13","-13","-13","-13","-13","-13","-13","-13","-13","-13","-13","-13"]
["Refrigerant charge","Refrigerant charge-=-Per circuit-=-TCO2Eq","","","TCO2Eq","29.2","32.4","34.4","41.8","50.1","54.3","54.3","54.3","64.7","64.7","64.7","73.1","75.2","86.6"]
["Compressor","Type","","","","Driven vapour compression","Driven vapour compression","Driven vapour compression","Driven vapour compression","Driven vapour compression","Driven vapour compression","Driven vapour compression","Driven vapour compression","Driven vapour compression","Driven vapour compression","Driven vapour compression","Driven vapour compression","Driven vapour compression","Driven vapour compression"]
["","Quantity","","","","4","4","4","4","4","4","4","4","4","4","4","6","6","6"]
["Weight","Operation weight","","","kg","2,017","2,317","2,594","2,736","2,914","3,014","3,085","3,185","3,208","3,326","3,344","4,166","4,288","4,716"]
["","Unit","","","kg","2,004","2,303","2,580","2,722","2,900","3,000","3,045","3,145","3,168","3,280","3,298","4,120","4,228","4,655"]
["Air heat exchanger","Type","","","","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type"]
["EER","","","","","3.123","3.073","3.077","3.051","3.003","3.003","2.916","2.916","3.007","2.988","2.959","2.963","2.903","2.95"]
["ESEER","","","","","4.53","4.64","4.51","4.6","4.53","4.68","4.44","4.63","4.68","4.64","4.54","4.82","4.69","4.65"]
["Refrigerant","GWP","","","","2,088","2,088","2,088","2,088","2,088","2,088","2,088","2,088","2,088","2,088","2,088","2,088","2,088","2,088"]
["","Type","","","","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A"]
["","Circuits","","Quantity","","2","2","2","2","2","2","2","2","2","2","2","2","2","2"]
["","Charge","","","kg","28","31","33","40","48","52","52","52","62","62","62","70","72","83"]
["Cooling capacity","Nom.","","","kW","165.4","187.9","211.4","235.8","304.2","304.2","339.9","339.9","385.1","407.1","432.6","502.3","579.4","645.1"]
["Water heat exchanger","Water volume","","","l","12","14","14","14","14","14","40","40","40","46","46","46","60","60"]
["","Type","","","","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger"]
["Power input","Cooling","","Nom.","kW","52.97","61.16","68.7","77.28","101.3","101.3","116.6","116.6","128.1","136.2","146.2","169.6","199.6","218.7"]
["Sound power level","Cooling","","Nom.","dBA","83","84","85","86","87","87","87","87","89","89","90","89","90","92"]
["Dimensions","Unit","","Width","mm","1,224","1,224","1,224","1,224","1,224","2,258","1,224","2,258","2,258","2,258","2,258","2,258","2,258","2,258"]
["","","","Depth","mm","4,413","4,413","5,313","5,313","6,213","3,210","6,213","3,210","4,110","4,110","4,110","5,010","5,010","5,910"]
["","","","Height","mm","2,271","2,271","2,271","2,271","2,271","2,221","2,271","2,221","2,221","2,221","2,221","2,221","2,221","2,221"]
["Capacity control","Minimum capacity","","","%","25","50","25","25","25","25","33","27","33","21","21","25","25","25"]
["","Method","","","","Staged","Staged","Staged","Staged","Staged","Staged","Staged","Staged","Staged","Staged","Staged","Staged","Staged","Staged"]
["Fan","Air flow rate","","Nom.","l/s","16,743","16,285","20,618","19,522","24,428","24,428","23,426","23,426","32,570","31,235","31,235","39,044","39,044","46,852"]
["","Speed","","","rpm","705","705","705","705","705","705","705","705","705","705","705","705","705","705"]
["Compressor","Starting method","","","","Direct on line","Direct on line","Direct on line","Direct on line","Direct on line","Direct on line","Direct on line","Direct on line","Direct on line","Direct on line","Direct on line","Direct on line","Direct on line","Direct on line"]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","400","400","400","400","400","400","400","400","400","400","400","400","400","400"]
["Notes","","","","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation."]
["","","","","","(2) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(2) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(2) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(2) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(2) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(2) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(2) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(2) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(2) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(2) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(2) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(2) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(2) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(2) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744"]
["","","","","","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water"]
["","","","","","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%."]
["","","","","","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced."]
["","","","","","(6) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(6) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(6) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(6) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(6) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(6) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(6) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(6) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(6) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(6) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(6) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(6) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(6) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(6) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current."]
["","","","","","(7) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(7) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(7) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(7) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(7) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(7) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(7) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(7) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(7) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(7) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(7) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(7) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(7) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(7) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current"]
["","","","","","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage."]
["","","","","","(9) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(9) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(9) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(9) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(9) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(9) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(9) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(9) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(9) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(9) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(9) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(9) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(9) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(9) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1"]
["","","","","","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS)."]
["","","","","","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels."]