{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":41,"n_cols":6,"rows_kept":41,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWHT-Q-XRA"]
[]
[]
[]
[]
["","","","","","EWHT100Q-XRA1"]
["Cooling capacity","Nom.","","","kW","91.68"]
["Capacity control","Method","","","","Step"]
["","Minimum capacity","","","%","50"]
["Power input","Cooling","","Nom.","kW","21.22"]
["EER","","","","","4.32"]
["IPLV","","","","","6.66"]
["SEER","","","","","5.98"]
["Dimensions","Unit","","Depth","mm","1300"]
["","","","Height","mm","1000"]
["","","","Width","mm","1200"]
["Weight","Operation weight","","","kg","502"]
["","Unit","","","kg","482"]
["Casing","Colour","","","","Ivory white"]
["","Material","","","","Galvanised steel"]
["Water heat exchanger - evaporator","Water pressure drop","Cooling","Nom.","kPa","17.7"]
["Compressor","Quantity","","","","2"]
["","Type","","","","Scroll"]
["Operation range","Water side","Evaporator","Min.","°CDB","-15"]
["","","","Max.","°CDB","30"]
["Sound power level","Cooling","","Nom.","dBA","74.99"]
["Sound pressure level","Cooling","","Nom.","dBA","59.36"]
["Refrigerant","Type","","","","R-32"]
["","GWP","","","","675"]
["","Charge","","","kg","7"]
["","Circuits","","Quantity","","1"]
["Piping connections","Evaporator water inlet/outlet (OD)","","","","3\""]
["Power supply","Phase","","","","3"]
["","Frequency","","","Hz","50"]
["","Voltage","","","V","400"]
["","Voltage range","","Min.","%","-10"]
["","","","Max.","%","+10"]
["Unit","Starting current","","Max","A","221"]
["","Running current","Cooling","Nom.","A","36.9"]
["","","","Max","A","62"]
["","Max unit current for wires sizing","","","A","68"]