{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":37,"n_cols":23,"rows_kept":37,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWLD-I-SS"]
[]
[]
[]
[]
["","","","","EWLD320I-SS","EWLD400I-SS","EWLD420I-SS","EWLD500I-SS","EWLD600I-SS","EWLD650I-SS","EWLD750I-SS","EWLD800I-SS","EWLD850I-SS","EWLD900I-SS","EWLD950I-SS","EWLDC10I-SS","EWLDC11I-SS","EWLDC12I-SS","EWLDC13I-SS","EWLDC14I-SS","EWLDC15I-SS","EWLDC16I-SS","EWLDC17I-SS"]
["Sound pressure level","Cooling","Nom.","dBA","75 (2)","76 (2)","78 (2)","78 (2)","78 (2)","78 (2)","79 (2)","80 (2)","81 (2)","81 (2)","81 (2)","80 (2)","80 (2)","81 (2)","81 (2)","83 (2)","83 (2)","83 (2)","83 (2)"]
["Sound power level","Cooling","Nom.","dBA","94","97","97","97","97","97","98","99","100","100","100","100","100","101","101","103","103","103","103"]
["Refrigerant","Circuits","Quantity","","1","1","1","1","2","2","2","2","2","2","2","3","3","3","3","3","3","3","3"]
["","Charge","","kg","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5"]
["","Type","","","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a"]
["Dimensions","Unit","Width","mm","1,464","1,464","1,464","1,464","1,464","1,464","1,464","1,464","1,464","1,464","1,464","2,135","2,135","2,135","2,135","2,135","2,135","2,135","2,135"]
["","","Depth","mm","3,114","3,114","3,114","3,114","4,391","4,391","4,391","4,391","4,391","4,391","4,391","4,426","4,426","4,426","4,426","4,426","4,426","4,426","4,426"]
["","","Height","mm","1,899","1,899","1,899","1,899","2,325","2,325","2,325","2,325","2,325","2,325","2,325","2,415","2,415","2,415","2,415","2,415","2,415","2,415","2,415"]
["Compressor","Type","","","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor"]
["","Quantity","","","1","1","1","1","2","2","2","2","2","2","2","3","3","3","3","3","3","3","3"]
["Capacity control","Minimum capacity","","%","25.0","25.0","25.0","25.0","12.5","12.5","12.5","12.5","12.5","12.5","12.5","8.3","8.3","8.3","8.3","8.3","8.3","8.3","8.3"]
["","Method","","","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless"]
["Weight","Operation weight","","kg","2,054","2,054","2,052","2,056","3,602","3,602","3,603","3,604","3,605","3,645","3,645","5,667","5,671","5,671","5,677","5,680","5,680","5,680","5,680"]
["","Unit","","kg","1,861","1,861","1,869","1,884","3,331","3,339","3,347","3,356","3,364","3,412","3,412","5,146","5,167","5,167","5,188","5,208","5,208","5,208","5,208"]
["Water heat exchanger - evaporator","Type","","","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube"]
["Cooling capacity","Nom.","","kW","315 (1)","374 (1)","437 (1)","509 (1)","607 (1)","670 (1)","740 (1)","802 (1)","865 (1)","935 (1)","975 (1)","1,029 (1)","1,097 (1)","1,144 (1)","1,210 (1)","1,278 (1)","1,330 (1)","1,381 (1)","1,433 (1)"]
["EER","","","","3.93 (1)","3.89 (1)","3.88 (1)","3.79 (1)","3.80 (1)","3.82 (1)","3.86 (1)","3.86 (1)","3.86 (1)","3.81 (1)","3.69 (1)","3.64 (1)","3.83 (1)","3.79 (1)","3.80 (1)","3.80 (1)","3.74 (1)","3.68 (1)","3.63 (1)"]
["Piping connections","Discharge line connection","","mm","88.9","88.9","88.9","88.9","88.9","88.9","88.9","88.9","88.9","88.9","88.9","88.9","88.9","88.9","88.9","88.9","88.9","88.9","88.9"]
["Power input","Cooling","Nom.","kW","80.3 (1)","96.0 (1)","113 (1)","134 (1)","160 (1)","175 (1)","192 (1)","208 (1)","224 (1)","246 (1)","264 (1)","283 (1)","286 (1)","302 (1)","318 (1)","336 (1)","356 (1)","375 (1)","395 (1)"]
["Power supply","Phase","","","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Frequency","","Hz","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50"]
["","Voltage","","V","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400"]
["Notes","","","","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation."]
["","","","","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744."]
["","","","","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water"]
["","","","","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%."]
["","","","","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load"]
["","","","","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current"]
["","","","","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope"]
["","","","","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage."]
["","","","","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1"]