{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":68,"n_cols":21,"rows_kept":68,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWLD-J-SS"]
[]
[]
[]
[]
["","","","","","EWLD110J-SS","EWLD130J-SS","EWLD145J-SS","EWLD165J-SS","EWLD195J-SS","EWLD235J-SS","EWLD265J-SS","EWLD290J-SS (Archived)","EWLD310J-SS (Archived)","EWLD330J-SS (Archived)","EWLD360J-SS (Archived)","EWLD390J-SS (Archived)","EWLD430J-SS (Archived)","EWLD470J-SS (Archived)","EWLD500J-SS (Archived)","EWLD530J-SS (Archived)"]
["Sound pressure level","Cooling","","Nom.","dBA","","","","","","","","82 (2)","82 (2)","82 (2)","82 (2)","82 (2)","82 (2)","82 (2)","82 (2)","83 (2)"]
["Sound power level","Cooling","","Nom.","dBA","","","","","","","","94","94","94","94","94","94","94","94","96"]
["Refrigerant","Circuits","","Quantity","","","","","","","","","2","2","2","2","2","2","2","2","2"]
["","GWP","","","","","","","","","","","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430"]
["","Type","","","","","","","","","","","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a"]
["Dimensions","Unit","","Width","mm","","","","","","","","913","913","913","913","913","913","913","913","913"]
["","","","Depth","mm","","","","","","","","2,684","2,684","2,684","2,684","2,684","2,684","2,684","2,684","2,684"]
["","","","Height","mm","","","","","","","","2,000","2,000","2,000","2,000","2,000","2,000","2,000","2,000","2,000"]
["Compressor","Type","","","","","","","","","","","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor"]
["","Quantity","","","","","","","","","","","2","2","2","2","2","2","2","2","2"]
["Capacity control","Minimum capacity","","","%","","","","","","","","12.5","12.5","12.5","12.5","12.5","12.5","12.5","12.5","12.5"]
["","Method","","","","","","","","","","","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless"]
["Weight","Operation weight","","","kg","","","","","","","","2,505","2,533","2,562","2,608","2,655","2,845","3,036","3,036","3,036"]
["","Unit","","","kg","","","","","","","","2,474","2,500","2,526","2,568","2,611","2,795","2,979","2,979","2,979"]
["Operation range","Condenser","Cooling","Min.","°CDB","","","","","","","","25","25","25","25","25","25","25","25","25"]
["","","","Max.","°CDB","","","","","","","","60","60","60","60","60","60","60","60","60"]
["","Evaporator","Cooling","Min.","°CDB","","","","","","","","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","","","Max.","°CDB","","","","","","","","15","15","15","15","15","15","15","15","15"]
["Water heat exchanger - evaporator","Type","","","","","","","","","","","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger"]
["Cooling capacity","Nom.","","","kW","","","","","","","","285 (1)","306 (1)","327 (1)","355 (1)","382 (1)","428 (1)","473 (1)","501 (1)","529 (1)"]
["EER","","","","","3.51 (1)","3.33 (1)","3.25 (1)","3.24 (1)","3.42 (1)","3.58 (1)","3.51 (1)","3.26 (1)","3.25 (1)","3.25 (1)","3.35 (1)","3.43 (1)","3.52 (1)","3.59 (1)","3.55 (1)","3.52 (1)"]
["Piping connections","Discharge line connection","","","inch","","","","","","","","4\"","4\"","4\"","4\"","4\"","4\"","4\"","4\"","4\""]
["Power input","Cooling","","Nom.","kW","","","","","","","","87.4 (1)","94.0 (1)","100 (1)","106 (1)","111 (1)","122 (1)","132 (1)","141 (1)","150 (1)"]
["Power supply","Phase","","","","","","","","","","","3~","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Frequency","","","Hz","","","","","","","","50","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","","","","","","","","400","400","400","400","400","400","400","400","400"]
["Notes","","","","","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation.","(1) - Cooling: entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C, unit at full load operation."]
["","","","","","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744.","(2) - Sound level data are measured at entering evaporator water temp. 12.0°C; leaving evaporator water temp. 7.0°C; condensing temperature 45.0°C; full load operation; standard: ISO3744."]
["","","","","","","","","","","","","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water","(3) - Fluid: Water"]
["","","","","","","","","","","","","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%."]
["","","","","","","","","","","","","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load"]
["","","","","","","","","","","","","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current"]
["","","","","","","","","","","","","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope"]
["","","","","","","","","","","","","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage."]
["","","","","","","","","","","","","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1"]
["","","","","","","","","","","","","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS)."]
["","","","","","","","","","","","","(11) - Its functioning relies on fluorinated greenhouse gases","(11) - Its functioning relies on fluorinated greenhouse gases","(11) - Its functioning relies on fluorinated greenhouse gases","(11) - Its functioning relies on fluorinated greenhouse gases","(11) - Its functioning relies on fluorinated greenhouse gases","(11) - Its functioning relies on fluorinated greenhouse gases","(11) - Its functioning relies on fluorinated greenhouse gases","(11) - Its functioning relies on fluorinated greenhouse gases","(11) - Its functioning relies on fluorinated greenhouse gases"]
["Cooling capacity","Nom.","","","kW","110 (1)","128 (1)","142 (1)","163 (1)","191 (1)","236 (1)","264 (1)"]
["Capacity control","Method","","","","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless"]
["","Minimum capacity","","","%","25.0","25.0","25.0","25.0","25.0","25.0","25.0"]
["Power input","Cooling","","Nom.","kW","31.2 (1)","38.4 (1)","43.8 (1)","50.4 (1)","56.0 (1)","66.0 (1)","75.3 (1)"]
["Dimensions","Unit","","Height","mm","1020","1020","1020","1020","1020","1020","1020"]
["","","","Width","mm","913","913","913","913","913","913","913"]
["","","","Depth","mm","2684","2684","2684","2684","2684","2684","2684"]
["Weight","Unit","","","kg","1124","1141","1237","1263","1305","1489","1489"]
["","Operation weight","","","kg","1138","1159","1253","1281","1327","1518","1518"]
["Water heat exchanger - evaporator","Type","","","","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger"]
["Compressor","Type","","","","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor"]
["","Quantity","","","","1","1","1","1","1","1","1"]
["Sound power level","Cooling","","Nom.","dBA","89","89","89","89","89","89","89"]
["Sound pressure level","Cooling","","Nom.","dBA","79 (2)","79 (2)","79 (2)","79 (2)","79 (2)","79 (2)","79 (2)"]
["Operation range","Evaporator","Cooling","Min.","°CDB","-10","-10","-10","-10","-10","-10","-10"]
["","","","Max.","°CDB","15","15","15","15","15","15","15"]
["","Condenser","Cooling","Min.","°CDB","25","25","25","25","25","25","25"]
["","","","Max.","°CDB","60","60","60","60","60","60","60"]
["Refrigerant","Type","","","","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a"]
["","GWP","","","","1430","1430","1430","1430","1430","1430","1430"]
["","Circuits","","Quantity","","1","1","1","1","1","1","1"]
["Piping connections","Discharge line connection","","","in","2\"1/2","4\"","4\"","4\"","4\"","4\"","4\""]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~","3~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50"]
["","Voltage","","","V","400","400","400","400","400","400","400"]