{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":42,"n_cols":10,"rows_kept":42,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWLQ-KBW1N"]
[]
[]
[]
[]
["","","","","","EWLQ014KBW1N","EWLQ025KBW1N","EWLQ033KBW1N","EWLQ049KBW1N","EWLQ064KBW1N"]
["Cooling capacity","Nom.","","","kW","12.05","21.87","27.96","43.4","56.71"]
["Capacity control","Minimum capacity","","","%","100","100","100","50","50"]
["Power input","Cooling","","Nom.","kW","3.54","6.42","8.26","12.74","16.2"]
["EER","","","","","3.402","3.406","3.386","3.406","3.501"]
["Dimensions","Unit","","Height","mm","600","600","600","600","600"]
["","","","Width","mm","600","600","600","600","600"]
["","","","Depth","mm","600","600","600","1200","1200"]
["Weight","Unit","","","kg","104","138","149","252","274"]
["","Operation weight","","","kg","105","140","152","257","280"]
["Water heat exchanger - evaporator","Type","","","","Brazed plate","Brazed plate","Brazed plate","Brazed plate","Brazed plate"]
["Compressor","Type","","","","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor"]
["","Quantity","","","","1","1","1","2","2"]
["Sound power level","Cooling","","Nom.","dBA","64","64","71","67","74"]
["Sound pressure level","Cooling","","Nom.","dBA","50","50","57","53","60"]
["Operation range","Evaporator","Cooling","Min.","°CDB","-10","-10","-10","-10","-10"]
["","","","Max.","°CDB","20","20","20","20","20"]
["","Condenser","Cooling","Min.","°CDB","25","25","25","25","25"]
["","","","Max.","°CDB","60","60","60","60","60"]
["Refrigerant","Type","","","","R-410A","R-410A","R-410A","R-410A","R-410A"]
["","Charge","","","kg","0","0","0","0","0"]
["","Circuits","","Quantity","","1","1","1","2","2"]
["Energy Efficiency Range","","","","","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F"]
["Power supply","Phase","","","","3~","3~","3~","3~","3~"]
["","Frequency","","","Hz","50","50","50","50","50"]
["","Voltage","","","V","400","400","400","400","400"]
["Notes","","","","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; condensing temp. bubble 45°C; liquid temp. 40°C; standard: Eurovent 6/C/003; condensing temp. bubble corresponds to compressor discharge pressure.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; condensing temp. bubble 45°C; liquid temp. 40°C; standard: Eurovent 6/C/003; condensing temp. bubble corresponds to compressor discharge pressure.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; condensing temp. bubble 45°C; liquid temp. 40°C; standard: Eurovent 6/C/003; condensing temp. bubble corresponds to compressor discharge pressure.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; condensing temp. bubble 45°C; liquid temp. 40°C; standard: Eurovent 6/C/003; condensing temp. bubble corresponds to compressor discharge pressure.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; condensing temp. bubble 45°C; liquid temp. 40°C; standard: Eurovent 6/C/003; condensing temp. bubble corresponds to compressor discharge pressure."]
["","","","","","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%."]
["","","","","","(3) - Maximum starting current: starting current of biggest compressor + current of the compressor at full load.","(3) - Maximum starting current: starting current of biggest compressor + current of the compressor at full load.","(3) - Maximum starting current: starting current of biggest compressor + current of the compressor at full load.","(3) - Maximum starting current: starting current of biggest compressor + current of the compressor at full load.","(3) - Maximum starting current: starting current of biggest compressor + current of the compressor at full load."]
["","","","","","(4) - Maximum running current is based on max compressor absorbed current in its envelope","(4) - Maximum running current is based on max compressor absorbed current in its envelope","(4) - Maximum running current is based on max compressor absorbed current in its envelope","(4) - Maximum running current is based on max compressor absorbed current in its envelope","(4) - Maximum running current is based on max compressor absorbed current in its envelope"]
["","","","","","(5) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(5) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(5) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(5) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(5) - Maximum unit current for wires sizing is based on minimum allowed voltage."]
["","","","","","(6) - Maximum current for wires sizing: compressor full load ampere x 1.1","(6) - Maximum current for wires sizing: compressor full load ampere x 1.1","(6) - Maximum current for wires sizing: compressor full load ampere x 1.1","(6) - Maximum current for wires sizing: compressor full load ampere x 1.1","(6) - Maximum current for wires sizing: compressor full load ampere x 1.1"]
["","","","","","(7) - Electrical data are subject to modification without notice. Please refer to unit nameplate data.","(7) - Electrical data are subject to modification without notice. Please refer to unit nameplate data.","(7) - Electrical data are subject to modification without notice. Please refer to unit nameplate data.","(7) - Electrical data are subject to modification without notice. Please refer to unit nameplate data.","(7) - Electrical data are subject to modification without notice. Please refer to unit nameplate data."]
["","","","","","(8) - Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511)","(8) - Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511)","(8) - Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511)","(8) - Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511)","(8) - Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511)"]
["","","","","","(9) - Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory","(9) - Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory","(9) - Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory","(9) - Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory","(9) - Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory"]
["","","","","","(10) - For specific information about additional options refer to the options section in the data book","(10) - For specific information about additional options refer to the options section in the data book","(10) - For specific information about additional options refer to the options section in the data book","(10) - For specific information about additional options refer to the options section in the data book","(10) - For specific information about additional options refer to the options section in the data book"]
["","","","","","(11) - Sound pressure level is measured in accordance with ISO3744. Sound power level is calculated from sound pressure level.","(11) - Sound pressure level is measured in accordance with ISO3744. Sound power level is calculated from sound pressure level.","(11) - Sound pressure level is measured in accordance with ISO3744. Sound power level is calculated from sound pressure level.","(11) - Sound pressure level is measured in accordance with ISO3744. Sound power level is calculated from sound pressure level.","(11) - Sound pressure level is measured in accordance with ISO3744. Sound power level is calculated from sound pressure level."]