{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":45,"n_cols":13,"rows_kept":45,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWWD-DZXS"]
[]
[]
[]
[]
["","","","","","EWWD320DZXSA1","EWWD440DZXSA1","EWWD530DZXSA1","EWWD610DZXSA2","EWWD640DZXSA2","EWWD700DZXSA1","EWWDC10DZXSA2","EWWDC14DZXSA2"]
["Cooling capacity","Nom.","","","kW","320","443","528","610","638","700","1056","1402"]
["Capacity control","Method","","","","Variable","Variable","Variable","Variable","Variable","Variable","Variable","Variable"]
["","Minimum capacity","","","%","30","21","21","16","15","18","11","9"]
["Power input","Cooling","","Nom.","kW","66.5","88.5","102","124.7","131","126","205","256"]
["EER","","","","","4.81","5","5.14","4.89","4.85","5.53","5.15","5.46"]
["Dimensions","Unit","","Depth","mm","3625","3625","3625","3625","3585","3585","3580","3580"]
["","","","Height","mm","1865","1865","1865","1985","1985","1985","2200","2200"]
["","","","Width","mm","1055","1055","1055","1160","1160","1160","1270","1270"]
["Weight","Unit","","","kg","1700","1900","2000","2850","2850","2600","3600","3800"]
["","Operation weight","","","kg","2033","2216","2347","3197","3344","3102","4292","4579"]
["Water heat exchanger - evaporator","Type","","","","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube"]
["","Water volume","","","l","70","96","107","107","134","134","199","229"]
["Water heat exchanger - condenser","Type","","","","Shell and tube","Shell and tube","Shell and tube","Shell and tube","Shell and tube","Shell and tube","Shell and tube","Shell and tube"]
["","Water flow rate","","Nom.","l/s","18.4","25.3","30.1","34.8","36.7","39.5","60.2","79.2"]
["Compressor","Type","","","","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor"]
["","Quantity","","","","1","1","1","2","2","1","2","2"]
["Sound power level","Cooling","","Nom.","dBA","88","89","90","91","91","91","93","94"]
["Sound pressure level","Cooling","","Nom.","dBA","70","71","72","73","73","73","75","76"]
["Operation range","Evaporator","Cooling","Min.","°CDB","4","4","4","4","4","4","4","4"]
["","","","Max.","°CDB","20","20","20","20","20","20","20","20"]
["","Condenser","Cooling","Min.","°CDB","20","20","20","20","20","20","20","20"]
["","","","Max.","°CDB","55","55","42","55","55","42","42","42"]
["Refrigerant","Type","","","","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a"]
["","Charge","","","kg","120","120","120","120","180","180","230","230"]
["","Circuits","","Quantity","","1","1","1","1","1","1","1","1"]
["","GWP","","","","1430","1430","1430","1430","1430","1430","1430","1430"]
["Refrigerant charge","Per circuit","","","tCO2Eq","171.6","171.6","171.6","171.6","185.9","257.4","328.9","328.9"]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","400","400","400","400","400","400","400","400"]
["Notes","","","","","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0"]
["","","","","","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%."]
["","","","","","(3) - In case of inverter driven units, no inrush current at start up is experienced.","(3) - In case of inverter driven units, no inrush current at start up is experienced.","(3) - In case of inverter driven units, no inrush current at start up is experienced.","(3) - In case of inverter driven units, no inrush current at start up is experienced.","(3) - In case of inverter driven units, no inrush current at start up is experienced.","(3) - In case of inverter driven units, no inrush current at start up is experienced.","(3) - In case of inverter driven units, no inrush current at start up is experienced.","(3) - In case of inverter driven units, no inrush current at start up is experienced."]
["","","","","","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C"]
["","","","","","(5) - Maximum current for wires sizing: compressor full load ampere x 1.1","(5) - Maximum current for wires sizing: compressor full load ampere x 1.1","(5) - Maximum current for wires sizing: compressor full load ampere x 1.1","(5) - Maximum current for wires sizing: compressor full load ampere x 1.1","(5) - Maximum current for wires sizing: compressor full load ampere x 1.1","(5) - Maximum current for wires sizing: compressor full load ampere x 1.1","(5) - Maximum current for wires sizing: compressor full load ampere x 1.1","(5) - Maximum current for wires sizing: compressor full load ampere x 1.1"]
["","","","","","(6) - All data are subject to change without notice. Please refer to the unit nameplate data.","(6) - All data are subject to change without notice. Please refer to the unit nameplate data.","(6) - All data are subject to change without notice. Please refer to the unit nameplate data.","(6) - All data are subject to change without notice. Please refer to the unit nameplate data.","(6) - All data are subject to change without notice. Please refer to the unit nameplate data.","(6) - All data are subject to change without notice. Please refer to the unit nameplate data.","(6) - All data are subject to change without notice. Please refer to the unit nameplate data.","(6) - All data are subject to change without notice. Please refer to the unit nameplate data."]
["","","","","","(7) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(7) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(7) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(7) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(7) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(7) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(7) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(7) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744"]
["","","","","","(8) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(8) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(8) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(8) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(8) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(8) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(8) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(8) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current"]
["","","","","","(9) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(9) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(9) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(9) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(9) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(9) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(9) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(9) - Maximum unit current for wires sizing is based on minimum allowed voltage."]