{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":50,"n_cols":11,"rows_kept":50,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWWS-J-SS"]
[]
[]
[]
[]
["","","","","","EWWS120J-SS","EWWS140J-SS","EWWS150J-SS","EWWS210J-SS","EWWS240J-SS","EWWS270J-SS"]
["Cooling capacity","Nom.","","","kW","115.2","136.3","154.7","207.3","241","272.2"]
["Capacity control","Method","","","","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless"]
["","Minimum capacity","","","%","25","25","25","25","25","25"]
["Power input","Cooling","","Nom.","kW","30","36.3","41.7","54.2","65.7","74.4"]
["EER","","","","","3.85","3.75","3.72","3.82","3.67","3.66"]
["IPLV","","","","","4.1","4.11","4.09","4.12","4.64","4.59"]
["SEER","","","","","3.36","3.38","3.32","3.39","3.87","3.82"]
["Dimensions","Unit","","Depth","mm","2684","2684","2684","2684","2684","2684"]
["","","","Height","mm","1020","1020","1020","1020","1020","1020"]
["","","","Width","mm","913","913","913","913","913","913"]
["Weight","Operation weight","","","kg","1211","1276","1378","1473","1663","1675"]
["","Unit","","","kg","1177","1233","1334","1416","1600","1607"]
["Casing","Colour","","","","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white"]
["","Material","","","","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet"]
["Water heat exchanger - evaporator","Type","","","","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger"]
["","Water volume","","","l","14","18","14","20","26","26"]
["","Water pressure drop","Cooling","Nom.","kPa","17.1","16.8","32.8","31.8","27.9","34.8"]
["Compressor","Quantity","","","","1","1","1","1","1","1"]
["","Type","","","","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor"]
["Operation range","Water side","Evaporator","Min.","°CDB","-10","-10","-10","-10","-10","-10"]
["","","","Max.","°CDB","15","15","15","15","15","15"]
["Sound power level","Cooling","","Nom.","dBA","95","95","95","95","95","95"]
["Sound pressure level","Cooling","","Nom.","dBA","79","79","79","79","79","79"]
["Refrigerant","GWP","","","","629.5","629.5","629.5","629.5","629.5","629.5"]
["","Charge","","","kg","18","35","34","37","38","38"]
["","Circuits","","Quantity","","1","1","1","1","1","1"]
["Piping connections","Evaporator water inlet/outlet (OD)","","","","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm"]
["Energy Efficiency Range","","","","","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F"]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~"]
["","Frequency","","","Hz","50","50","50","50","50","50"]
["","Voltage","","","V","400","400","400","400","400","400"]
["","Voltage range","","Min.","%","-10","-10","-10","-10","-10","-10"]
["","","","Max.","%","10","10","10","10","10","10"]
["Unit","Starting current","","Max","A","154","154","198","198","291","291"]
["","Running current","Cooling","Nom.","A","50","60","70","87","105","117"]
["","","","Max","A","81","96","108","141","164","185"]
["","Max unit current for wires sizing","","","A","89","107","120","158","183","207"]
["Notes","","","","","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB"]
["","","","","","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB"]
["","","","","","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)"]
["","","","","","(5) - According to EN14825","(5) - According to EN14825","(5) - According to EN14825","(5) - According to EN14825","(5) - According to EN14825","(5) - According to EN14825"]
["","","","","","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual."]
["","","","","","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing"]