{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":94,"n_cols":19,"rows_kept":94,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWYD-BZSL"]
[]
[]
[]
[]
["","","","","","EWYD250BZSL","EWYD270BZSL","EWYD290BZSL","EWYD320BZSL","EWYD330BZSL","EWYD360BZSL","EWYD370BZSL","EWYD400BZSL","EWYD430BZSL","EWYD450BZSL","EWYD490BZSL","EWYD530BZSLB3","EWYD510BZSL","EWYD570BZSLB3"]
["Cooling capacity","Nom.","","","kW","","","","","","","","","","","","519","","569"]
["Capacity control","Method","","","","","","","","","","","","","","","Variable","","Variable"]
["","Minimum capacity","","","%","","","","","","","","","","","","9","","9"]
["Power input","Cooling","","Nom.","kW","","","","","","","","","","","","185","","217"]
["EER","","","","","2.76","2.66","2.62","2.75","2.68","2.64","2.57","2.66","2.59","2.83","2.77","2.8","2.73","2.62"]
["IPLV","","","","","4.90","4.96","4.91","5.17","5.08","5.12","5.06","5.22","5.13","5.07","5.03","4.99","4.99","4.89"]
["SEER","","","","","","","","","","","","","","","","4.6","","4.55"]
["Dimensions","Unit","","Depth","mm","","","","","","","","","","","","6,659","","6,659"]
["","","","Height","mm","","","","","","","","","","","","2,280","","2,280"]
["","","","Width","mm","","","","","","","","","","","","2,254","","2,254"]
["Weight","Operation weight","","","kg","","","","","","","","","","","","6,474","","6,463"]
["","Unit","","","kg","","","","","","","","","","","","6,245","","6,245"]
["Casing","Colour","","","","","","","","","","","","","","","Ivory white","","Ivory white"]
["","Material","","","","","","","","","","","","","","","Galvanized and painted steel sheet","","Galvanized and painted steel sheet"]
["Air heat exchanger","Type","","","","","","","","","","","","","","","High efficiency fin and tube type","","High efficiency fin and tube type"]
["Fan","Quantity","","","","","","","","","","","","","","","12","","12"]
["","Type","","","","","","","","","","","","","","","Direct propeller","","Direct propeller"]
["Fan motor","Drive","","","","","","","","","","","","","","","Direct on line","","Direct on line"]
["Compressor","Quantity","","","","","","","","","","","","","","","3","","3"]
["","Type","","","","","","","","","","","","","","","Single screw compressor","","Single screw compressor"]
["","Starting method","","","","","","","","","","","","","","","Inverter driven","","Inverter driven"]
["Sound power level","Cooling","","Nom.","dBA","","","","","","","","","","","","97","","97"]
["Sound pressure level","Cooling","","Nom.","dBA","","","","","","","","","","","","77.2","","77.2"]
["Refrigerant","Type","","","","","","","","","","","","","","","R-134a","","R-134a"]
["","GWP","","","","","","","","","","","","","","","1,430.0","","1,430.0"]
["","Charge","","","kg","","","","","","","","","","","","141","","147"]
["","Circuits","","Quantity","","","","","","","","","","","","","3","","3"]
["Piping connections","Evaporator water inlet/outlet (OD)","","","","","","","","","","","","","","","219.1mm","","219.1mm"]
["Power supply","Phase","","","","","","","","","","","","","","","3~","","3~"]
["","Frequency","","","Hz","","","","","","","","","","","","50","","50"]
["","Voltage","","","V","","","","","","","","","","","","400","","400"]
["","Voltage range","","Min.","%","","","","","","","","","","","","-10","","-10"]
["","","","Max.","%","","","","","","","","","","","","10","","10"]
["Unit","Starting current","","Max","A","","","","","","","","","","","","0","","0"]
["","Running current","Cooling","Nom.","A","","","","","","","","","","","","305","","305"]
["","","","Max","A","","","","","","","","","","","","447","","447"]
["","Max unit current for wires sizing","","","A","","","","","","","","","","","","492","","492"]
["Cooling capacity","Nom.","","","kW","247","265","290","315","330","353","370","401","423","446","490","","507"]
["Capacity control","Method","","","","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","","Stepless"]
["","Minimum capacity","","","%","13.0","13.0","13.0","13.0","13.0","13.0","13.0","13.0","13.0","9.0","9.0","","9.0"]
["Power input","Cooling","","Nom.","kW","89.5","99.5","110","115","123","134","144","151","163","158","177","","186"]
["Dimensions","Unit","","Depth","mm","3547","3547","3547","4428","4428","4428","4428","5329","5329","6659","6659","","6659"]
["","","","Height","mm","2335","2335","2335","2335","2335","2335","2335","2335","2335","2280","2280","","2280"]
["","","","Width","mm","2254","2254","2254","2254","2254","2254","2254","2254","2254","2254","2254","","2254"]
["Weight","Operation weight","","","kg","3888","3933","3978","4343","4343","4408","4478","4858","4858","5765","6234","","6474"]
["","Unit","","","kg","3750","3795","3840","4210","4210","4280","4350","4730","4730","5525","6005","","6245"]
["Casing","Colour","","","","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","","Ivory white"]
["","Material","","","","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","","Galvanized and painted steel sheet"]
["Air heat exchanger","Type","","","","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","","High efficiency fin and tube type with integral subcooler"]
["Fan","Quantity","","","","6","6","6","8","8","8","8","10","10","12","12","","12"]
["","Type","","","","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","","Direct propeller"]
["","Air flow rate","Cooling","Nom.","l/s","24432","24264","24095","32576","32576","32628","32127","40720","40720","48863","48415","","47732"]
["Fan motor","Drive","","","","DOL","DOL","DOL","DOL","DOL","DOL","DOL","DOL","DOL","DOL","DOL","","DOL"]
["Compressor","Quantity","","","","2","2","2","2","2","2","2","2","2","3","3","","3"]
["","Type","","","","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","","Single screw compressor"]
["","Starting method","","","","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","","VFD driven"]
["Operation range","Air side","Cooling","Min.","°CDB","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","","-10"]
["","","","Max.","°CDB","45","45","45","45","45","45","45","45","45","45","45","","45"]
["","Water side","Evaporator","Min.","°CDB","-8","-8","-8","-8","-8","-8","-8","-8","-8","-8","-8","","-8"]
["","","","Max.","°CDB","15","15","15","15","15","15","15","15","15","15","15","","15"]
["Sound power level","Cooling","","Nom.","dBA","94","94","94","95","95","95","95","95","95","97","97","","97"]
["Sound pressure level","Cooling","","Nom.","dBA","76","76","76","76","76","76","76","76","76","77","77","","77"]
["Refrigerant","Type","","","","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","","R-134a"]
["","GWP","","","","1430","1430","1430","1430","1430","1430","1430","1430","1430","1430","1430","","1430"]
["","Circuits","","Quantity","","2","2","2","2","2","2","2","2","2","3","3","","3"]
["Piping connections","Evaporator water inlet/outlet (OD)","","","","139.7mm","139.7mm","139.7mm","139.7mm","139.7mm","139.7mm","139.7mm","139.7mm","139.7mm","219.1mm","219.1mm","","219.1mm"]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","","3~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50","50","50","50","","50"]
["","Voltage","","","V","400","400","400","400","400","400","400","400","400","400","400","","400"]
["","Voltage range","","Min.","%","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","","-10"]
["","","","Max.","%","10","10","10","10","10","10","10","10","10","10","10","","10"]
["Unit","Starting current","","Max","A","0","0","0","0","0","0","0","0","0","0","288","","311"]
["","Running current","Cooling","Nom.","A","147","161","177","187","201","217","230","244","261","258","263","","275"]
["","","","Max","A","216","216","216","261","298","298","298","334","362","336","381","","415"]
["","Max unit current for wires sizing","","","A","238","238","238","287","328","328","328","367","398","370","381","","415"]
["Notes","","","","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation."]
["","","","","","(2) - Heating: air exchanger 7.0 - 90%°C; water exchanger 50.0/45.0, unit at full load operation.","(2) - Heating: air exchanger 7.0 - 90%°C; water exchanger 50.0/45.0, unit at full load operation.","(2) - Heating: air exchanger 7.0 - 90%°C; water exchanger 50.0/45.0, unit at full load operation.","(2) - Heating: air exchanger 7.0 - 90%°C; water exchanger 50.0/45.0, unit at full load operation.","(2) - Heating: air exchanger 7.0 - 90%°C; water exchanger 50.0/45.0, unit at full load operation.","(2) - Heating: air exchanger 7.0 - 90%°C; water exchanger 50.0/45.0, unit at full load operation.","(2) - Heating: air exchanger 7.0 - 90%°C; water exchanger 50.0/45.0, unit at full load operation.","(2) - Heating: air exchanger 7.0 - 90%°C; water exchanger 50.0/45.0, unit at full load operation.","(2) - Heating: air exchanger 7.0 - 90%°C; water exchanger 50.0/45.0, unit at full load operation.","(2) - Heating: air exchanger 7.0 - 90%°C; water exchanger 50.0/45.0, unit at full load operation.","(2) - Heating: air exchanger 7.0 - 90%°C; water exchanger 50.0/45.0, unit at full load operation.","","(2) - Heating: air exchanger 7.0 - 90%°C; water exchanger 50.0/45.0, unit at full load operation."]
["","","","","","(3) - SCOP is based on the following conditions: Tbivalent +2°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825.","(3) - SCOP is based on the following conditions: Tbivalent +2°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825.","(3) - SCOP is based on the following conditions: Tbivalent +2°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825.","(3) - SCOP is based on the following conditions: Tbivalent +2°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825.","(3) - SCOP is based on the following conditions: Tbivalent +2°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825.","(3) - SCOP is based on the following conditions: Tbivalent +2°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825.","(3) - SCOP is based on the following conditions: Tbivalent +2°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825.","(3) - SCOP is based on the following conditions: Tbivalent +2°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825.","(3) - SCOP is based on the following conditions: Tbivalent +2°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825.","(3) - SCOP is based on the following conditions: Tbivalent +2°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825.","(3) - SCOP is based on the following conditions: Tbivalent +2°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825.","","(3) - SCOP is based on the following conditions: Tbivalent +2°C, Tdesign -10°C, Average ambient conditions, Ref. EN14825."]
["","","","","","(4) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(4) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(4) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(4) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(4) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(4) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(4) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(4) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(4) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(4) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(4) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","","(4) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744"]
["","","","","","(5) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(5) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(5) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(5) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(5) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(5) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(5) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(5) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(5) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(5) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(5) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","","(5) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%."]
["","","","","","(6) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(6) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(6) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(6) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(6) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(6) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(6) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(6) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(6) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(6) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(6) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","","(6) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced."]
["","","","","","(7) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(7) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(7) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(7) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(7) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(7) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(7) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(7) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(7) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(7) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(7) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","","(7) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current."]
["","","","","","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage."]
["","","","","","(9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","","(9) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current"]
["","","","","","(10) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(10) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(10) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(10) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(10) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(10) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(10) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(10) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(10) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(10) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(10) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","","(10) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1"]
["","","","","","(11) - Fluid: Water","(11) - Fluid: Water","(11) - Fluid: Water","(11) - Fluid: Water","(11) - Fluid: Water","(11) - Fluid: Water","(11) - Fluid: Water","(11) - Fluid: Water","(11) - Fluid: Water","(11) - Fluid: Water","(11) - Fluid: Water","","(11) - Fluid: Water"]
["","","","","","(12) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(12) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(12) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(12) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(12) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(12) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(12) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(12) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(12) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(12) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(12) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","","(12) - For more details on the operating limits please refer to the Chiller Selection Software (CSS)."]
["","","","","","(13) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(13) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(13) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(13) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(13) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(13) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(13) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(13) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(13) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(13) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(13) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","","(13) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels."]