{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":39,"n_cols":8,"rows_kept":39,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FDQ-B"]
[]
[]
[]
[]
["","","","","","FDQ125B8V3B9","FDQ200B8V3B9","FDQ250B8V3B9"]
["Cooling capacity","Total capacity","","Nom.","kW","","20.0","24.1"]
["Heating capacity","Total capacity","","Nom.","kW","","23.0","26.4"]
["Casing","Colour","","","","Unpainted","Unpainted","Unpainted"]
["","Material","","","","Galvanised steel","Galvanised steel","Galvanised steel"]
["Dimensions","Unit","","Height","mm","350","450","450"]
["","","","Width","mm","1,400","1,400","1,400"]
["","","","Depth","mm","662","900","900"]
["Weight","Unit","","","kg","59.0","89.0","94.0"]
["Required ceiling void >","mm","","","","350","450","450"]
["Fan","Air flow rate","Cooling","Nom.","m³/min","43.0"]
["","","","Medium","m³/min","","69.0","89.0"]
["","","Heating","Nom.","m³/min","43.0"]
["","","","Medium","m³/min","","69.0","89.0"]
["","External static pressure","","High","Pa","150","250","250"]
["","","","Nom.","Pa","150","250","250"]
["","","","Low","Pa","150","250","250"]
["Sound power level","Cooling","","","dBA","75.0","81.0","82.0"]
["Sound pressure level","Cooling","","High","dBA","44.0","45.0","47.0"]
["","Heating","","Low","dBA","44.0","45.0","47.0"]
["Piping connections","Liquid","","OD","mm","9.52","9.52","12.70"]
["","Gas","","OD","mm","15.9","22.2","22.2"]
["","Drain","","","","","OD Ø25.0","OD Ø25.0"]
["Control systems","Wired remote control","","","","","BRC1D52, BRC1E52A/B","BRC1D52, BRC1E52A/B"]
["Standard Accessories","Installation and operation manual","","","","1","1","1"]
["Power supply","Name","","","","V3","V3","V3"]
["","Phase","","","","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50"]
["","Voltage","","","V","230","230 +/-10%","230 +/-10%"]
["Notes","","","","","(1) - Sound values are measured in a semi-anechoic room with corrections.","(1) - Sound values are measured in a semi-anechoic room with corrections.","(1) - Sound values are measured in a semi-anechoic room with corrections."]
["","","","","","(2) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(2) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(2) - The sound pressure level is measured via a microphone at 1m distance of the unit."]
["","","","","","(3) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(3) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(3) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings."]
["","","","","","(4) - The sound power level is an absolute value indicating the power which a sound source generates.","(4) - The sound power level is an absolute value indicating the power which a sound source generates.","(4) - The sound power level is an absolute value indicating the power which a sound source generates."]
["","","","","","(5) - For more details, please refer to wiring diagram, name plate and installation manual.","(5) - For more details, please refer to wiring diagram, name plate and installation manual.","(5) - For more details, please refer to wiring diagram, name plate and installation manual."]