{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":29,"n_cols":13,"rows_kept":29,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FTXM-M / RXM-M"]
[]
[]
[]
[]
["","","","","FTXM20M2V1B / RXM20M2V1B","FTXM25M2V1B / RXM25M2V1B","FTXM35M2V1B / RXM35M2V1B","FTXM42M2V1B / RXM42M2V1B","FTXM42M2V1B / RXM42MV1B","FTXM50M2V1B / RXM50M2V1B","FTXM50M2V1B / RXM50MV1B","FTXM60M2V1B / RXM60M2V1B","FTXM71M2V1B / RXM71M2V1B"]
["Cooling capacity","Min.","","kW","1.3","1.3","1.4","1.70","1.7","1.70","1.7","1.9","2.30"]
["","Max.","","kW","2.6","3.2","4.0","5.00","5.0","5.30","5.3","6.7","8.50"]
["","Nom.","","kW","2.0","2.5","3.40","4.20","4.2","5.00","5.00","6.00","7.10"]
["Space cooling","SEER","","","8.53","8.52","8.51","7.50","7.50","7.33","7.33","6.90","6.11"]
["","Annual energy consumption","","kWh/a","83","103","140","196","196","239","239","304","407"]
["","Capacity","Pdesign","kW","2.00","2.50","3.40","4.20","4.20","5.00","5.00","6.00","7.10"]
["","Energy efficiency class","","","A+++","A+++","A+++","A++","A++","A++","A++","A++","A++"]
["Space heating (Average climate)","Capacity","Pdesign","kW","2.30","2.40","2.50","4.00","4.00","4.60","4.60","4.60","6.20"]
["","SCOP/A","","","5.10","5.10","5.10","4.60","4.60","4.60","4.60","4.30","3.81"]
["","Energy efficiency class","","","A+++","A+++","A+++","A++","A++","A++","A++","A+","A"]
["","Pdh Heating capacity at -10°","","kW","2.24","2.3","2.35","3.68","3.68","4.09","4.09"]
["","Annual energy consumption","","kWh/a","632","659","686","1,216","1,216","1,400","1,400","1,496","2,276"]
["Nominal efficiency","Annual energy consumption","","kWh","219","278","421","","560","","679","885"]
["","EER","","","4.57","4.50","4.23","3.75","3.75","3.68","3.68","3.39","3.03"]
["","COP","","","5.00","5.00","4.40","4.12","4.12","4.00","4.00","3.61","3.19"]
["","Energy labeling Directive","Cooling","","A","A","A","A","A","A","A","A","B"]
["","","Heating","","A","A","A","A","A","A","A","A","D"]
["Heating capacity","Nom.","","kW","2.50","2.8","4.00","5.40","5.40","5.80","5.8","7.00","8.20"]
["","Min.","","kW","1.3","1.3","1.4","1.70","1.7","1.70","1.7","1.7","2.30"]
["","Max.","","kW","3.5","4.70","5.2","6.00","6.0","6.50","6.5","8.0","10.20"]
["Notes","","","","(1) - EER/COP according to Eurovent 2012, for use outside EU only","(1) - EER/COP according to Eurovent 2012, for use outside EU only","(1) - EER/COP according to Eurovent 2012, for use outside EU only","(1) - See separate drawing for electrical data","(1) - EER/COP according to Eurovent 2012, for use outside EU only","(1) - See separate drawing for electrical data","(1) - EER/COP according to Eurovent 2012, for use outside EU only","(1) - EER/COP according to Eurovent 2012, for use outside EU only","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB, 24°CWB; equivalent piping length: 5m"]
["","","","","(2) - Nominal efficiency: cooling at 35°/27° nominal load, heating at 7°/20° nominal load","(2) - Nominal efficiency: cooling at 35°/27° nominal load, heating at 7°/20° nominal load","(2) - Nominal efficiency: cooling at 35°/27° nominal load, heating at 7°/20° nominal load","(2) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m.","(2) - Nominal efficiency: cooling at 35°/27° nominal load, heating at 7°/20° nominal load","(2) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m.","(2) - Nominal efficiency: cooling at 35°/27° nominal load, heating at 7°/20° nominal load","(2) - Nominal efficiency: cooling at 35°/27° nominal load, heating at 7°/20° nominal load","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 5m"]
["","","","","","","","(3) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m.","","(3) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m.","","","(3) - See separate drawing for electrical data"]