{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":30,"n_cols":13,"rows_kept":30,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FTXM-M / RXM-N9"]
[]
[]
[]
[]
["","","","","FTXM20M2V1B / RXM20N5V1B9","FTXM20M2V1B / RXM20N2V1B9","FTXM25M2V1B / RXM25N5V1B9","FTXM25M2V1B / RXM25N2V1B9","FTXM35M2V1B / RXM35N2V1B9","FTXM35M2V1B / RXM35N5V1B9","FTXM42M2V1B / RXM42N2V1B9","FTXM50M2V1B / RXM50N2V1B9","FTXM60M2V1B / RXM60N2V1B9"]
["Outdoor unit","","","","RXM20N5V1B9","RXM20N2V1B9","RXM25N5V1B9","RXM25N2V1B9","RXM35N2V1B9","RXM35N5V1B9","RXM42N2V1B9","RXM50N2V1B9","RXM60N2V1B9"]
["Cooling capacity","Min.","","kW","1.3","1.3","1.3","1.3","1.4","1.4","1.70","1.70","1.90"]
["","Nom.","","kW","2.0","2.0","2.5","2.5","3.4","3.4","4.20","5.00","6.00"]
["","Max.","","kW","2.6","2.6","3.2","3.2","4.0","4.0","5.00","5.30","6.70"]
["Heating capacity","Min.","","kW","1.30","1.30","1.30","1.30","1.40","1.40","1.70","1.70","1.70"]
["","Nom.","","kW","2.50","2.50","2.80","2.80","4.00","4.00","5.40","5.80","7.00"]
["","Max.","","kW","3.50","3.50","4.70","4.70","5.20","5.20","6.00","6.50","8.00"]
["Nominal efficiency","Annual energy consumption","","kWh","220","220","280","280","400","400"]
["","COP","","","5.00","5.00","5.00","5.00","4.04","4.04","4.12","4.00","3.61"]
["","EER","","","4.57","4.57","4.50","4.50","4.23","4.23","3.75","3.68","3.39"]
["","Energy labeling Directive","Cooling","","A","A","A","A","A","A","A","A","A"]
["","","Heating","","A","A","A","A","A","A","A","A","A"]
["Space cooling","Annual energy consumption","","kWh/a","83","83","103","103","140","140","196","239","304"]
["","Energy efficiency class","","","A+++","A+++","A+++","A+++","A+++","A+++","A++","A++","A++"]
["","Capacity","Pdesign","kW","2.00","2.00","2.50","2.50","3.40","3.40","4.20","5.00","6.00"]
["","SEER","","","8.53","8.53","8.52","8.52","8.51","8.51","7.50","7.33","6.90"]
["Space heating (Average climate)","Annual energy consumption","","kWh/a","632","632","659","659","686","686","1,216","1,400","1,496"]
["","Capacity","Pdesign","kW","2.30","2.30","2.40","2.40","2.50","2.50","4.00","4.60","4.60"]
["","Energy efficiency class","","","A+++","A+++","A+++","A+++","A+++","A+++","A++","A++","A+"]
["","Pdh Heating capacity at -10°","","kW","2.24","2.24","2.30","2.30","2.35","2.35","3.68","4.09","4.09"]
["","SCOP/A","","","5.10","5.10","5.10","5.10","5.10","5.10","4.60","4.60","4.30"]
["Notes","","","","(1) - See separate drawing for electrical data","(1) - See separate drawing for electrical data","(1) - See separate drawing for electrical data","(1) - See separate drawing for electrical data","(1) - See separate drawing for electrical data","(1) - See separate drawing for electrical data","(1) - See separate drawing for electrical data","(1) - See separate drawing for electrical data","(1) - See separate drawing for electrical data"]
["","","","","(2) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m.","(2) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m.","(2) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m.","(2) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m.","(2) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m.","(2) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m.","(2) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m.","(2) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m.","(2) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m."]
["","","","","(3) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m.","(3) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m.","(3) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m.","(3) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m.","(3) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m.","(3) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m.","(3) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m.","(3) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m.","(3) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m."]