{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":51,"n_cols":14,"rows_kept":51,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWA-AF"]
[]
[]
[]
[]
["","","","","","FWA01AF","FWA02AF","FWA03AF","FWA04AF","FWA05AF","FWA06AF","FWA07AF","FWA08AF","FWA10AF"]
["Sound pressure level","Super high","","","dBA","35","41","45","42","48","52","52","51","54"]
["","Low","","","dBA","27","26","27","29","34","37","39","37","42"]
["","High","","","dBA","33","40","43","41","47","50","51","50","53"]
["Total sound power level","Super high","","","dBA","46","52","56","53","59","63","63","62","65"]
["","Low","","","dBA","38","37","38","40","45","48","50","48","53"]
["","High","","","dBA","44","51","54","52","58","61","62","61","64"]
["Water flow","Cooling","","Super high","l/h","352","456","592","729","868","1,131","1,262","1,455","1,890"]
["","","","Low","l/h","229","263","315","458","592","773","886","995","1,347"]
["","","","High","l/h","331","448","577","703","862","1,089","1,199","1,420","1,852"]
["","Heating","","High","l/h","210","268","340","434","520","637","772","884","1,108"]
["","","","Super high","l/h","221","276","348","448","524","659","808","904","1,128"]
["","","","Low","l/h","154","172","199","298","372","469","594","647","833"]
["","Water pressure drop","Heating","Super high","kPa","5","8","14","25","33","61","18","24","42"]
["","","","High","kPa","3","4","5","7","8","10","12","13","17"]
["","","","Low","kPa","3","4","6","15","23","41","13","17","30"]
["","","Cooling","Super high","kPa","9","15","28","17","23","41","13","18","32"]
["","","","High","kPa","8","14","26","15","22","39","12","17","31"]
["","","","Low","kPa","4","6","9","7","11","21","7","9","17"]
["Piping connections","Drain","","OD","mm","R 3/4\"","R 3/4\"","R 3/4\"","R 3/4\"","R 3/4\"","R 3/4\"","R 3/4\"","R 3/4\"","R 3/4\""]
["","Water","","Inlet","","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\""]
["","","","Outlet","","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\""]
["Power input","High","","","kW","0.042","0.058","0.073","0.076","0.105","0.149","0.206","0.215","0.273"]
["","Low","","","kW","0.04","0.04","0.05","0.05","0.07","0.12","0.17","0.17","0.22"]
["","Super high","","","kW","0.043","0.059","0.072","0.075","0.107","0.155","0.208","0.219","0.276"]
["Dimensions","Unit","","Width","mm","590","590","590","590","590","590","590","590","590"]
["","","","Depth","mm","705","735","875","1,010","1,010","1,210","1,400","1,560","1,820"]
["","","","Height","mm","253","253","253","253","253","253","253","253","253"]
["Casing","Colour","","","","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal"]
["Weight","Unit","","","kg","18.0","19.0","22.0","26.0","26.0","31.0","42.0","43.0","50.0"]
["Cooling capacity (standard conditions)","Total capacity 4-pipe","","Low","kW","1.33","1.53","1.84","2.67","3.46","4.51","5.17","5.81","7.86"]
["","","","High","kW","1.93","2.61","3.37","4.10","5.03","6.36","6.99","8.28","10.81"]
["","","","Super high","kW","2.06","2.66","3.46","4.26","5.07","6.60","7.36","8.49","11.03"]
["","Sensible capacity 4-pipe","","Low","kW","1.01","1.15","1.33","2.00","2.63","3.36","4.13","4.52","6.01"]
["","","","Super high","kW","1.59","2.07","2.61","3.30","3.99","5.08","6.05","6.82","8.69"]
["","","","High","kW","1.49","2.03","2.54","3.17","3.96","4.88","5.72","6.64","8.50"]
["Heating capacity (standard conditions)","Capacity 4-pipe","","Low","kW","1.57","1.77","2.05","3.07","3.83","4.83","6.11","6.65","8.58"]
["","","","Super high","kW","2.27","2.84","3.57","4.61","5.38","6.79","8.29","9.29","11.60"]
["","","","High","kW","2.15","2.75","3.49","4.46","5.35","6.56","7.93","9.08","11.39"]
["Current input","High","","","A","0.18","0.26","0.32","0.33","0.46","0.65","0.90","0.94","1.20"]
["","Super high","","","A","0.19","0.26","0.32","0.33","0.47","0.68","0.91","0.96","1.21"]
["","Low","","","A","0.17","0.18","0.22","0.22","0.29","0.51","0.73","0.73","0.96"]
["Power supply","Type","","","","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50"]
["","Phase","","","","1~","1~","1~","1~","1~","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240"]