{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":51,"n_cols":14,"rows_kept":51,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWA-AT"]
[]
[]
[]
[]
["","","","","","FWA01AT","FWA02AT","FWA03AT","FWA04AT","FWA05AT","FWA06AT","FWA07AT","FWA08AT","FWA10AT"]
["Sound pressure level","Super high","","","dBA","35","41","45","42","48","52","52","51","54"]
["","Low","","","dBA","26","25","27","29","34","35","39","36","41"]
["","High","","","dBA","33","40","43","41","47","50","51","49","53"]
["Total sound power level","Super high","","","dBA","46","52","56","53","59","63","63","62","65"]
["","Low","","","dBA","37","36","38","40","45","46","50","47","52"]
["","High","","","dBA","44","51","54","52","58","61","62","60","64"]
["Water flow","Cooling","","Super high","l/h","363","456","612","737","906","1,159","1,278","1,455","1,930"]
["","","","Low","l/h","232","263","320","472","610","776","890","995","1,347"]
["","","","High","l/h","342","445","596","705","892","1,109","1,220","1,420","1,892"]
["","Heating","","High","l/h","342","445","596","705","892","1,109","1,220","1,420","1,892"]
["","","","Super high","l/h","363","456","612","737","906","1,159","1,278","1,455","1,930"]
["","","","Low","l/h","232","263","320","472","610","776","890","995","1,347"]
["","Water pressure drop","Heating","Super high","kPa","9","14","26","16","25","37","12","15","26"]
["","","","High","kPa","8","13","24","14","24","34","11","14","25"]
["","","","Low","kPa","3","4","6","6","10","15","5","6","12"]
["","","Cooling","Super high","kPa","9","15","29","17","24","43","14","18","33"]
["","","","High","kPa","8","14","28","16","24","40","12","17","32"]
["","","","Low","kPa","4","6","9","8","12","21","7","9","17"]
["Piping connections","Drain","","OD","mm","R 3/4\"","R 3/4\"","R 3/4\"","R 3/4\"","R 3/4\"","R 3/4\"","R 3/4\"","R 3/4\"","R 3/4\""]
["","Water","","Inlet","","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\""]
["","","","Outlet","","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\""]
["Power input","High","","","kW","0.042","0.059","0.072","0.072","0.105","0.159","0.209","0.219","0.286"]
["","Low","","","kW","0.04","0.04","0.05","0.05","0.07","0.12","0.17","0.17","0.23"]
["","Super high","","","kW","0.042","0.059","0.073","0.075","0.110","0.163","0.216","0.222","0.288"]
["Dimensions","Unit","","Width","mm","590","590","590","590","590","590","590","590","590"]
["","","","Depth","mm","705","735","875","1,010","1,010","1,210","1,400","1,560","1,820"]
["","","","Height","mm","253","253","253","253","253","253","253","253","253"]
["Casing","Colour","","","","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal"]
["Weight","Unit","","","kg","17.0","18.0","21.0","24.0","24.0","30.0","40.0","41.0","47.0"]
["Cooling capacity (standard conditions)","Sensible capacity 2-pipe","","Super high","kW","1.65","2.07","2.71","3.34","4.18","5.22","6.14","6.82","8.89"]
["","","","Low","kW","1.03","1.15","1.35","2.07","2.72","3.38","4.15","4.52","6.01"]
["","","","High","kW","1.55","2.01","2.63","3.18","4.11","4.97","5.83","6.64","8.70"]
["","Total capacity 2-pipe","","Super high","kW","2.12","2.66","3.57","4.30","5.28","6.76","7.46","8.49","11.26"]
["","","","Low","kW","1.36","1.53","1.87","2.75","3.56","4.53","5.19","5.81","7.86"]
["","","","High","kW","2.00","2.60","3.48","4.12","5.21","6.47","7.12","8.28","11.04"]
["Heating capacity (standard conditions)","Capacity 2-pipe","","High","kW","2.27","2.97","3.81","4.69","6.13","7.28","8.90","9.99","12.95"]
["","","","Super high","kW","2.44","3.06","3.93","4.92","6.24","7.66","9.38","10.28","13.26"]
["","","","Low","kW","1.46","1.61","1.91","3.00","3.98","4.85","6.28","6.71","8.79"]
["Current input","High","","","A","0.18","0.26","0.32","0.32","0.46","0.70","0.92","0.96","1.26"]
["","Super high","","","A","0.18","0.26","0.32","0.33","0.48","0.72","0.95","0.97","1.26"]
["","Low","","","A","0.16","0.18","0.22","0.24","0.29","0.53","0.74","0.75","1.00"]
["Power supply","Type","","","","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50"]
["","Phase","","","","1~","1~","1~","1~","1~","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240"]