{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":49,"n_cols":13,"rows_kept":49,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWB-CTN"]
[]
[]
[]
[]
["","","","","","FWB04CATN6V3","FWB05CATN6V3","FWB06CATN6V3","FWB08CATN6V3","FWB10CATN6V3","FWB11CATN6V3","FWB15CATN6V3","FWB17CATN6V3"]
["Sound pressure level","Low","","","dBA","20.0 (4)","31.0 (5)","31.0 (5)","30.0 (4)","30.0 (4)","30.0 (4)","53.0 (4)","53.0 (4)"]
["","High","","","dBA","44.0 (4)","46.0 (5)","46.0 (5)","50.0 (4)","50.0 (4)","50.0 (4)","61.0 (4)","61.0 (4)"]
["Total sound power level","Low","","","dBA","28.0 (4)","39.0 (4)","39.0 (4)","38.0 (4)","38.0 (4)","38.0 (4)","61.0 (4)","61.0 (4)"]
["","High","","","dBA","52.0 (4)","54.0 (4)","54.0 (4)","58.0 (4)","58.0 (4)","58.0 (4)","69.0 (4)","69.0 (4)"]
["Water flow","Cooling","","Low","l/h","160 (1)","222 (1)","274 (1)","343 (1)","394 (1)","482 (1)","1,095 (1)","1,225 (1)"]
["","","","High","l/h","340 (1)","408 (1)","527 (1)","664 (1)","828 (1)","930 (1)","1,295 (1)","1,448 (1)"]
["","Heating","","High","l/h","346 (2)","408 (2)","528 (2)","749 (2)","898 (2)","955 (2)","1,357 (2)","1,472 (2)"]
["","","","Low","l/h","153 (2)","231 (2)","276 (2)","408 (2)","442 (2)","457 (2)","1,162 (2)","1,248 (2)"]
["","Water pressure drop","Heating","High","kPa","5 (2)","7 (2)","8 (2)","11 (2)","8 (2)","11 (2)","16 (2)","23 (2)"]
["","","","Low","kPa","1 (2)","2 (2)","2 (2)","4 (2)","2 (2)","3 (2)","12 (2)","17 (2)"]
["","","Cooling","High","kPa","6 (1)","8 (1)","9 (1)","11 (1)","8 (1)","12 (1)","18 (1)","26 (1)"]
["","","","Low","kPa","2 (1)","3 (1)","3 (1)","3 (1)","2 (1)","3 (1)","13 (1)","20 (1)"]
["Piping connections","Drain","","OD","mm","17","17","17","17","17","17","17","17"]
["","Water","","Inlet","","1/2\"","1/2\"","1/2\"","1/2\"","3/4\"","3/4\"","3/4\"","3/4\""]
["","","","Outlet","","1/2\"","1/2\"","1/2\"","1/2\"","3/4\"","3/4\"","3/4\"","3/4\""]
["Power input","High","","","kW","0.082","0.106","0.105","0.192","0.192","0.192","0.332","0.332"]
["","Low","","","kW","0.024","0.034","0.034","0.076","0.076","0.076","0.235","0.235"]
["Allowed water temperature","Heating","","Max.","°C","80.000","80.000","80.000","80.000","80.000","80.000","80.000","80.000"]
["","Cooling","","Min.","°C","5","5","5","5","5","5","5","5"]
["Dimensions","Unit","","Width","mm","758","758","968","968","1,178","1,178","1,178","1,178"]
["","","","Depth","mm","665","665","665","665","745","745","745","745"]
["","","","Height","mm","250","250","250","250","280","280","280","280"]
["Water connections","Primary coil","","","inch","1/2\"","1/2\"","1/2\"","1/2\"","3/4 \"","3/4 \"","3/4 \"","3/4 \""]
["Weight","Unit","","","kg","24.4","25.4","33.0","36.0","45.0","45.0","51.0","51.0"]
["Fan","Air flow rate","","Low","m³/h","109","171","195","305","333","333","1,050","1,050"]
["","","","High","m³/h","276","341","402","652","760","760","1,289","1,289"]
["","Available static pressure","","High","Pa","63","77","63","75","61","61","60","60"]
["","","","Low","Pa","10","19","19","17","12","12","40","40"]
["Cooling capacity (standard conditions)","Sensible capacity 2-pipe","","Low","kW","0.61 (1)","0.89 (1)","1.07 (1)","1.42 (1)","1.60 (1)","1.70 (1)","4.51 (1)","4.83 (1)"]
["","","","High","kW","1.34 (1)","1.59 (1)","2.03 (1)","2.81 (1)","3.39 (1)","3.64 (1)","5.29 (1)","5.67 (1)"]
["","Total capacity 2-pipe","","Low","kW","0.92 (1)","1.27 (1)","1.57 (1)","1.92 (1)","2.22 (1)","2.44 (1)","6.15 (1)","6.91 (1)"]
["","","","High","kW","1.90 (1)","2.27 (1)","2.96 (1)","2.68 (1)","4.63 (1)","5.23 (1)","7.21 (1)","8.12 (1)"]
["Heating capacity (standard conditions)","Capacity 2-pipe","","High","kW","1.99 (2)","2.35 (2)","3.10 (2)","4.31 (2)","5.17 (2)","5.49 (2)","7.80 (2)","8.46 (2)"]
["","","","Low","kW","0.88 (2)","1.33 (2)","1.59 (2)","2.35 (2)","2.54 (2)","2.63 (2)","6.68 (2)","7.18 (2)"]
["Power supply","Type","","","","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50"]
["","Phase","","","","1~","1~","1~","1~","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","230","230","230","230","230","230","230","230"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K."]
["","","","","","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K."]
["","","","","","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K."]
["","","","","","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741"]
["","","","","","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit."]