{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":74,"n_cols":13,"rows_kept":74,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWE-DATN5V3-R"]
[]
[]
[]
[]
["","","","","","FWE03DATN5V3-R","FWE04DATN5V3-R","FWE05DATN5V3-R","FWE06DATN5V3-R","FWE07DATN5V3-R","FWE08DATN5V3-R","FWE10DATN5V3-R","FWE11DATN5V3-R"]
["Sound pressure level","Fan speed 1","","","dBA","21.0","22.0","22.0","20.0","21.0","21.0","27.0","29.0"]
["","Low","","","dBA","21.0","23.0","27.0","29.0","24.0","24.0","33.0","34.0"]
["","Fan speed 6","","","dBA","","","","40.0","40.0","40.0","47.0","49.0"]
["","High","","","dBA","35.0","34.0","40.0","40.0","40.0","40.0","47.0","49.0"]
["Standard Accessories","Installation manual","","","","1","1","1","1","1","1","1","1"]
["Total sound power level","Low","","","dBA","32.0","34.0","37.0","39.0","34.0","34.0","43.0","44.0"]
["","Fan speed 1","","","dBA","32.0","32.0","32.0","30.0","31.0","31.0","38.0","40.0"]
["","Fan speed 6","","","dBA","","","","50.0","50.0","50.0","57.0","59.0"]
["","High","","","dBA","45.0","44.0","50.0","50.0","50.0","50.0","57.0","59.0"]
["Water flow","Cooling","","Low","l/h","210","241","282","345","415","477","534","583"]
["","","","Fan speed 1","l/h","210","209","228","213","354","409","442","483"]
["","","","Fan speed 6","l/h","","","","536","589","674","897","962"]
["","","","High","l/h","334","354","443","536","589","674","897","962"]
["","Heating","","Fan speed 1","l/h","230","275","289","366","471","550","579","620"]
["","","","Fan speed 6","l/h","","","","689","751","797","1,029","1,092"]
["","","","High","l/h","344","409","496","689","751","797","1,029","1,092"]
["","","","Low","l/h","230","306","341","505","542","613","669","717"]
["","Water pressure drop","Heating","Fan speed 1","kPa","8.52","7.00","7.00","5.00","15.00","15.00","17.00","19.00"]
["","","","High","kPa","18.59","15.05","22.22","16.99","36.92","28.69","45.14","50.28"]
["","","","Fan speed 6","kPa","","","","16.99","36.92","28.69","45.14","50.28"]
["","","","Low","kPa","8.52","8.33","10.38","8.65","19.91","18.19","21.14","23.85"]
["","","Cooling","Fan speed 6","kPa","","","","8.85","13.48","18.67","29.00","33.09"]
["","","","High","kPa","13.18","10.09","14.35","8.85","13.48","18.67","29.00","33.09"]
["","","","Fan speed 1","kPa","6.05","4.00","3.00","1.00","4.00","9.00","8.00","9.00"]
["","","","Low","kPa","6.05","5.00","5.53","3.23","5.96","10.90","11.07","13.00"]
["Piping connections","Drain","","OD","mm","17.3","17.3","17.3","17.3","17.3","17.3","17.3","17.3"]
["","Water","","Inlet","","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\""]
["","","","Outlet","","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\""]
["Power input","Fan speed 6","","","kW","","","","0.062","0.067","0.067","0.104","0.110"]
["","Fan speed 1","","","kW","0.026","0.026","0.026","0.039","0.029","0.029","0.026","0.028"]
["","High","","","kW","0.033","0.032","0.039","0.062","0.067","0.067","0.104","0.110"]
["","Low","","","kW","0.026","0.028","0.029","0.043","0.037","0.037","0.036","0.039"]
["Allowed water temperature","Heating","","Max.","°C","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000"]
["","","","Min.","°C","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00"]
["","Cooling","","Min.","°C","5","5","5","5","5","5","5","5"]
["","","","Max.","°C","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0"]
["Dimensions","Unit","","Width","mm","795","795","795","995","1,195","1,195","1,195","1,195"]
["","","","Depth","mm","610","610","610","610","610","610","610","610"]
["","","","Height","mm","200","200","200","200","200","200","200","200"]
["Casing","Colour","","","","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal"]
["Weight","Unit","","","kg","17.5","18.5","18.5","22.0","25.5","25.5","25.5","25.5"]
["Fan","Air flow rate","","Fan speed 1","m³/h","235","227","243","290","397","397","436","489"]
["","","","Fan speed 6","m³/h","","","","677","725","725","1,032","1,116"]
["","","","Low","m³/h","235","263","304","446","481","481","555","619"]
["","","","High","m³/h","407","385","488","677","725","725","1,032","1,116"]
["","Available static pressure","","Fan speed 1","Pa","27","27","25","25","28","28","22","25"]
["","","","High","Pa","55","57","55","60","60","60","63","65"]
["","","","Fan speed 6","Pa","","","","60","60","60","63","65"]
["","","","Low","Pa","27","33","32","41","34","34","32","34"]
["Cooling capacity (standard conditions)","Sensible capacity 2-pipe","","Fan speed 6","kW","","","","2.56","2.81","3.21","4.28","4.59"]
["","","","Low","kW","1.00","1.15","1.35","1.64","1.98","2.27","2.54","2.78"]
["","","","Fan speed 1","kW","1.00","0.99","1.09","1.02","1.70","1.95","2.11","2.31"]
["","","","High","kW","1.59","1.69","2.11","2.56","2.81","3.21","4.28","4.59"]
["","Total capacity 2-pipe","","Fan speed 6","kW","","","","3.12","3.42","3.92","5.22","5.59"]
["","","","Low","kW","1.22","1.40","1.64","2.00","2.42","2.77","3.10","3.39"]
["","","","High","kW","1.94","2.06","2.58","3.12","3.42","3.92","5.22","5.59"]
["","","","Fan speed 1","kW","1.22","1.21","1.33","1.24","2.07","2.38","2.57","2.81"]
["Heating capacity (standard conditions)","Capacity 2-pipe","","High","kW","2.00","2.38","2.89","4.00","4.37","4.64","5.98","6.35"]
["","","","Fan speed 6","kW","","","","4.00","4.37","4.64","5.98","6.35"]
["","","","Low","kW","1.34","1.78","1.98","2.85","3.15","3.56","3.89","4.17"]
["","","","Fan speed 1","kW","1.34","1.60","1.68","2.06","2.74","3.20","3.37","3.60"]
["Power supply","Type","","","","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50"]
["","Phase","","","","1~","1~","1~","1~","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","230","230","230","230","230","230","230","230"]
["Notes","","","","","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB"]
["","","","","","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K."]
["","","","","","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K."]