{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":49,"n_cols":8,"rows_kept":49,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWF-CT"]
[]
[]
[]
[]
["","","","","","FWF02CATNMV1","FWF03CATNMV1","FWF04CATNMV1"]
["Sound pressure level","Low","","","dBA","29 (5)","30 (5)","36 (5)"]
["","High","","","dBA","42 (5)","45 (5)","48 (5)"]
["Total sound power level","Low","","","dBA","39 (4)","41 (4)","45 (4)"]
["","High","","","dBA","52 (4)","54 (4)","56 (4)"]
["Water flow","Cooling","","Low","l/h","460","780","810"]
["","","","High","l/h","460","780","810"]
["","Heating","","High","l/h","460","780","810"]
["","","","Low","l/h","460","780","810"]
["","Water pressure drop","Heating","High","kPa","23","22","25"]
["","","","Low","kPa","13","9","13"]
["","","Cooling","High","kPa","19","27","29"]
["","","","Low","kPa","19","27","29"]
["Piping connections","Drain","","OD","mm","19.05","19.05","19.05"]
["","Water","","Inlet","","19.05 mm","19.05 mm","19.05 mm"]
["","","","Outlet","","19.05 mm","19.05 mm","19.05 mm"]
["Power input","High","","","kW","0.063","0.064","0.079"]
["","Low","","","kW","0.05","0.05","0.07"]
["Dimensions","Unit","","Width","mm","570","570","570"]
["","","","Depth","mm","570","570","570"]
["","","","Height","mm","250","250","250"]
["Weight","Unit","","","kg","15.0","17.0","17.0"]
["Cooling capacity (standard conditions)","Sensible capacity 2-pipe","","Low","kW","1.39 (1)","1.83 (1)","2.22 (1)"]
["","","","High","kW","1.85 (1)","2.87 (1)","3.09 (1)"]
["","Total capacity 2-pipe","","Low","kW","1.86 (1)","2.73 (1)","3.11 (1)"]
["","","","High","kW","2.43 (1)","4.04 (1)","4.20 (1)"]
["Decoration panel","Dimensions","Unit","Height","mm","45","45","45"]
["","","","Depth","mm","460","460","460"]
["","","","Width","mm","460","460","460"]
["Heating capacity (standard conditions)","Capacity 2-pipe","","High","kW","3.03 (2)","3.88 (2)","4.37 (2)"]
["","","","Low","kW","2.08 (2)","2.18 (2)","2.91 (2)"]
["Current input","High","","","A","0.28","0.28","0.35"]
["","Low","","","A","0.21","0.24","0.31"]
["Power supply","Type","","","","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50"]
["","Phase","","","","1N~","1N~","1N~"]
["","Frequency","","","Hz","50","50","50"]
["","Voltage","","","V","220-240","220-240","220-240"]
["Fan motor","Power input","","Low","kW","0.046","0.052","0.069"]
["","","","High","kW","0.063","0.064","0.079"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K."]
["","","","","","(2) - Heating: 2 pipe: air 20°CDB; entering water 50°C","(2) - Heating: 2 pipe: air 20°CDB; entering water 50°C","(2) - Heating: 2 pipe: air 20°CDB; entering water 50°C"]
["","","","","","(3) - Air flow at 0Pa ESP","(3) - Air flow at 0Pa ESP","(3) - Air flow at 0Pa ESP"]
["","","","","","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741"]
["","","","","","(5) - Sound pressure measured at 1,5m below the facia (JIS B 8615)","(5) - Sound pressure measured at 1,5m below the facia (JIS B 8615)","(5) - Sound pressure measured at 1,5m below the facia (JIS B 8615)"]