{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":54,"n_cols":13,"rows_kept":54,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWF-D"]
[]
[]
[]
[]
["","","","","","FWF02DATN5V3--","FWF02DAFN5V3--","FWF03DATN5V3--","FWF03DAFN5V3--","FWF04DATN5V3--","FWF04DAFN5V3--","FWF05DATN5V3--","FWF05DAFN5V3--"]
["Cooling capacity (standard conditions)","Sensible capacity 2-pipe","","Low","kW","1.09","","1.75","","1.91","","2.11"]
["","","","High","kW","1.76","","2.31","","3.01","","3.88"]
["","Sensible capacity 4-pipe","","Low","kW","","1.20","","1.61","","1.78","","1.85"]
["","","","High","kW","","1.76","","2.19","","2.88","","3.67"]
["","Total capacity 2-pipe","","Low","kW","1.30","","2.37","","2.65","","2.93"]
["","","","High","kW","2.00","","3.00","","4.07","","5.10"]
["","Total capacity 4-pipe","","Low","kW","","1.44","","2.30","","2.58","","2.64"]
["","","","High","kW","","2.00","","3.00","","4.00","","5.02"]
["Heating capacity (standard conditions)","Capacity 2-pipe","","Low","kW","1.56","","2.44","","2.69","","2.95"]
["","","","High","kW","2.54","","3.30","","4.26","","5.74"]
["","Capacity 4-pipe","","Low","kW","","2.23","","2.78","","2.90","","2.99"]
["","","","High","kW","","3.31","","4.15","","4.59","","5.64"]
["Power input","Low","","","kW","0.01","0.01","0.01","0.02","0.01","0.02","0.02","0.02"]
["","High","","","kW","0.018","0.017","0.019","0.019","0.024","0.024","0.045","0.047"]
["Dimensions","Unit","","Height","mm","260","260","260","260","260","260","260","260"]
["","","","Width","mm","642","642","642","642","642","642","642","642"]
["","","","Depth","mm","575","575","575","575","575","575","575","575"]
["Weight","Unit","","","kg","14.5","16.0","15.5","17.0","15.5","17.0","15.5","17.0"]
["Fan","Air flow rate","","Low","m³/h","278","301","363","356","369","361","408","367"]
["","","","High","m³/h","498","477","516","534","623","612","860","847"]
["Total sound power level","Low","","","dBA","33.0","34.0","36.0","36.0","36.0","38.0","39.0","40.0"]
["","High","","","dBA","41.0","41.0","42.0","44.0","47.0","48.0","54.0","56.0"]
["Sound pressure level","Low","","","dBA","19.0","20.0","22.0","22.0","22.0","24.0","25.0","26.0"]
["","High","","","dBA","27.0","27.0","28.0","30.0","33.0","34.0","40.0","42.0"]
["Water flow","Cooling","","Low","l/h","224","248","407","396","455","444","504","455"]
["","","","High","l/h","344","345","515","516","699","687","878","864"]
["","Heating","","High","l/h","437","285","568","357","733","395","987","485"]
["","","","Low","l/h","269","192","419","239","463","249","507","257"]
["","Water pressure drop","Cooling","Low","kPa","6","7","18","17","16","15","18","16"]
["","","","High","kPa","8","8","25","25","29","28","41","41"]
["","","Heating","Low","kPa","6","7","21","5","15","5","18","6"]
["","","","High","kPa","11","10","32","8","30","9","50","12"]
["Allowed water temperature","Cooling","","Min.","°C","5","5","5","5","5","5","5","5"]
["","","","Max.","°C","75.0","75.0","75.0","75.0","75.0","75.0","75.0","75.0"]
["","Heating","","Min.","°C","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00"]
["","","","Max.","°C","75.000","75.000","75.000","75.000","75.000","75.000","75.000","75.000"]
["Piping connections","Water","","Inlet","","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)"]
["","","","Outlet","","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)"]
["","Drain","","OD","mm","VP20 (External dia.26, Internal dia. 20)","VP20 (External dia.26, Internal dia. 20)","VP20 (External dia.26, Internal dia. 20)","VP20 (External dia.26, Internal dia. 20)","VP20 (External dia.26, Internal dia. 20)","VP20 (External dia.26, Internal dia. 20)","VP20 (External dia.26, Internal dia. 20)","VP20 (External dia.26, Internal dia. 20)"]
["Power supply","Type","","","","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50"]
["","Phase","","","","1~","1~","1~","1~","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","230","230","230","230","230","230","230","230"]
["Notes","","","","","(1) - Cooling: air 27°CDB, 19°CWB; entering water 7°C; leaving water 12°C","(1) - Cooling: air 27°CDB, 19°CWB; entering water 7°C; leaving water 12°C","(1) - Cooling: air 27°CDB, 19°CWB; entering water 7°C; leaving water 12°C","(1) - Cooling: air 27°CDB, 19°CWB; entering water 7°C; leaving water 12°C","(1) - Cooling: air 27°CDB, 19°CWB; entering water 7°C; leaving water 12°C","(1) - Cooling: air 27°CDB, 19°CWB; entering water 7°C; leaving water 12°C","(1) - Cooling: air 27°CDB, 19°CWB; entering water 7°C; leaving water 12°C","(1) - Cooling: air 27°CDB, 19°CWB; entering water 7°C; leaving water 12°C"]
["","","","","","(2) - Heating: 2 pipe: air 20°CDB, 15°CWB; entering water 45°C; leaving water 40°C","(2) - Heating: 2 pipe: air 20°CDB, 15°CWB; entering water 45°C; leaving water 40°C","(2) - Heating: 2 pipe: air 20°CDB, 15°CWB; entering water 45°C; leaving water 40°C","(2) - Heating: 2 pipe: air 20°CDB, 15°CWB; entering water 45°C; leaving water 40°C","(2) - Heating: 2 pipe: air 20°CDB, 15°CWB; entering water 45°C; leaving water 40°C","(2) - Heating: 2 pipe: air 20°CDB, 15°CWB; entering water 45°C; leaving water 40°C","(2) - Heating: 2 pipe: air 20°CDB, 15°CWB; entering water 45°C; leaving water 40°C","(2) - Heating: 2 pipe: air 20°CDB, 15°CWB; entering water 45°C; leaving water 40°C"]
["","","","","","(3) - Heating: 4 pipe: air 20°CDB, 15°CWB; entering water 65°C; leaving water 55°C","(3) - Heating: 4 pipe: air 20°CDB, 15°CWB; entering water 65°C; leaving water 55°C","(3) - Heating: 4 pipe: air 20°CDB, 15°CWB; entering water 65°C; leaving water 55°C","(3) - Heating: 4 pipe: air 20°CDB, 15°CWB; entering water 65°C; leaving water 55°C","(3) - Heating: 4 pipe: air 20°CDB, 15°CWB; entering water 65°C; leaving water 55°C","(3) - Heating: 4 pipe: air 20°CDB, 15°CWB; entering water 65°C; leaving water 55°C","(3) - Heating: 4 pipe: air 20°CDB, 15°CWB; entering water 65°C; leaving water 55°C","(3) - Heating: 4 pipe: air 20°CDB, 15°CWB; entering water 65°C; leaving water 55°C"]
["","","","","","(4) - The unit is not pre-charged. A minimal rest charge is present related to factory quality inspection","(4) - The unit is not pre-charged. A minimal rest charge is present related to factory quality inspection","(4) - The unit is not pre-charged. A minimal rest charge is present related to factory quality inspection","(4) - The unit is not pre-charged. A minimal rest charge is present related to factory quality inspection","(4) - The unit is not pre-charged. A minimal rest charge is present related to factory quality inspection","(4) - The unit is not pre-charged. A minimal rest charge is present related to factory quality inspection","(4) - The unit is not pre-charged. A minimal rest charge is present related to factory quality inspection","(4) - The unit is not pre-charged. A minimal rest charge is present related to factory quality inspection"]
["","","","","","(5) - Airflow value measurements are performed at 20C (DB) /15 C(WB) condition.","(5) - Airflow value measurements are performed at 20C (DB) /15 C(WB) condition.","(5) - Airflow value measurements are performed at 20C (DB) /15 C(WB) condition.","(5) - Airflow value measurements are performed at 20C (DB) /15 C(WB) condition.","(5) - Airflow value measurements are performed at 20C (DB) /15 C(WB) condition.","(5) - Airflow value measurements are performed at 20C (DB) /15 C(WB) condition.","(5) - Airflow value measurements are performed at 20C (DB) /15 C(WB) condition.","(5) - Airflow value measurements are performed at 20C (DB) /15 C(WB) condition."]