{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":53,"n_cols":11,"rows_kept":53,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWG-AT"]
[]
[]
[]
[]
["","","","","","FWG05AATNMV1","FWG05AT","FWG08AATNMV1","FWG08AT","FWG11AATNMV1","FWG11AT"]
["Sound pressure level","Low","","","dBA","23 (5)","23 (5)","37 (6)","37 (6)","41 (6)","41 (6)"]
["","High","","","dBA","37 (5)","37 (5)","47 (6)","47 (6)","51 (6)","51 (6)"]
["Total sound power level","Low","","","dBA","34 (4)","34 (4)","49 (4)","49 (4)","49 (4)","49 (4)"]
["","High","","","dBA","46 (4)","46 (4)","57 (4)","57 (4)","59 (4)","59 (4)"]
["Water flow","Cooling","","Low","l/h","1,030","1,030","1,530","1,530","2,040","2,040"]
["","","","High","l/h","1,030","1,030","1,530","1,530","2,040","2,040"]
["","Heating","","High","l/h","1,030","1,030","1,530","1,530","2,040","2,040"]
["","","","Low","l/h","1,030","1,030","1,530","1,530","2,040","2,040"]
["","Water pressure drop","Heating","High","kPa","21","21","20","20","35","35"]
["","","","Low","kPa","12","12","10","10","18","18"]
["","","Cooling","High","kPa","24","24","20","20","41","41"]
["","","","Low","kPa","10","10","9","9","22","22"]
["Piping connections","Drain","","OD","mm","19","19","19","19","19","19"]
["","Water","","Inlet","","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\""]
["","","","Outlet","","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\""]
["Power input","High","","","kW","0.047","0.049","0.100","0.093","0.130","0.130"]
["","Low","","","kW","0.02","0.02","0.04","0.03","0.05","0.05"]
["Dimensions","Unit","","Width","mm","820","820","820","820","820","820"]
["","","","Depth","mm","820","820","820","820","820","820"]
["","","","Height","mm","265","265","265","265","300","300"]
["Casing","Colour","","","","Without powder paint","Without powder paint","Without powder paint","Without powder paint","Without powder paint","Without powder paint"]
["Weight","Unit","","","kg","26.0","26.0","28.0","28.0","32.0","32.0"]
["Fan","Air flow rate","","Low","m³/h","","595 (3)","","951 (3)","","1,155 (3)"]
["","","","High","m³/h","","1,053 (3)","","1,512 (3)","","1,801 (3)"]
["Cooling capacity (standard conditions)","Sensible capacity 2-pipe","","Low","kW","2.53 (1)","2.53 (1)","4.23 (1)","4.23 (1)","5.50 (1)","5.50 (1)"]
["","","","High","kW","4.47 (1)","4.47 (1)","6.34 (1)","6.34 (1)","8.25 (1)","8.25 (1)"]
["","Total capacity 2-pipe","","Low","kW","3.49 (1)","3.49 (1)","5.77 (1)","5.77 (1)","7.81 (1)","7.81 (1)"]
["","","","High","kW","5.86 (1)","5.86 (1)","8.71 (1)","8.71 (1)","11.63 (1)","11.63 (1)"]
["Decoration panel","Dimensions","Unit","Height","mm","85","85","85","85","85","85"]
["","","","Depth","mm","990","990","990","990","990","990"]
["","","","Width","mm","990","990","990","990","990","990"]
["Heating capacity (standard conditions)","Capacity 2-pipe","","High","kW","5.91 (2)","7.10 (2)","9.40 (2)","11.20 (2)","11.35 (2)","13.70 (2)"]
["","","","Low","kW","3.73 (2)","4.75 (2)","5.95 (2)","7.60 (2)","7.66 (2)","9.65 (2)"]
["Current input","High","","","A","0.26","0.26","0.74","0.74","0.95","0.95"]
["","Low","","","A","0.13","0.13","0.28","0.28","0.35","0.35"]
["Power supply","Type","","","","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50"]
["","Phase","","","","1N~","1N~","1N~","1N~","1N~","1N~"]
["","Frequency","","","Hz","50","50","50","50","50","50"]
["","Voltage","","","V","220-240","220-240","220-240","220-240","220-240","220-240"]
["Fan motor","Power input","","Low","kW","0.022","0.022","0.036","0.036","0.049","0.049"]
["","","","High","kW","0.047","0.047","0.100","0.100","0.130","0.130"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K."]
["","","","","","(2) - Heating: 2 pipe: air 20°CDB; entering water 50°C","(2) - Heating: 2 pipe: air 20°CDB; entering water 50°C","(2) - Heating: 2 pipe: air 20°CDB; entering water 50°C","(2) - Heating: 2 pipe: air 20°CDB; entering water 50°C","(2) - Heating: 2 pipe: air 20°CDB; entering water 50°C","(2) - Heating: 2 pipe: air 20°CDB; entering water 50°C"]
["","","","","","(3) - Air flow at 0Pa ESP","(3) - Air flow at 0Pa ESP","(3) - Air flow at 0Pa ESP","(3) - Air flow at 0Pa ESP","(3) - Air flow at 0Pa ESP","(3) - Air flow at 0Pa ESP"]
["","","","","","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741"]
["","","","","","(5) - Sound pressure level measured at 1.4m below the facia (JIS C 9612).","(5) - Sound pressure level measured at 1.4m below the facia (JIS C 9612).","(5) - Sound pressure level measured at 1.4m below the facia (JIS C 9612).","(5) - Sound pressure level measured at 1.4m below the facia (JIS C 9612).","(5) - Sound pressure level measured at 1.4m below the facia (JIS C 9612).","(5) - Sound pressure level measured at 1.4m below the facia (JIS C 9612)."]
["","","","","","(6) - Sound pressure measured at 1,5m below the facia (JIS B 8615)","(6) - Sound pressure measured at 1,5m below the facia (JIS B 8615)","(6) - Sound pressure measured at 1,5m below the facia (JIS B 8615)","(6) - Sound pressure measured at 1,5m below the facia (JIS B 8615)","(6) - Sound pressure measured at 1,5m below the facia (JIS B 8615)","(6) - Sound pressure measured at 1,5m below the facia (JIS B 8615)"]