{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":52,"n_cols":10,"rows_kept":52,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWH-AF"]
[]
[]
[]
[]
["","","","","","FWH02AAFN6V3","FWH03AAFN6V3","FWH04AAFN6V3","FWH06AAFN6V3","FWH08AAFN6V3"]
["Cooling capacity (standard conditions)","Sensible capacity 4-pipe","","Low","kW","1.24 (1)","1.49 (1)","2.00 (1)","3.47 (1)","4.29 (1)"]
["","","","High","kW","1.94 (1)","3.38 (1)","3.02 (1)","5.81 (1)","6.98 (1)"]
["","Total capacity 4-pipe","","Low","kW","1.56 (1)","2.01 (1)","2.58 (1)","4.73 (1)","5.83 (1)"]
["","","","High","kW","2.35 (1)","3.38 (1)","3.62 (1)","7.45 (1)","9.00 (1)"]
["Heating capacity (standard conditions)","Capacity 4-pipe","","Low","kW","2.53 (3)","2.75 (3)","3.67 (3)","7.20 (3)","8.64 (3)"]
["","","","High","kW","3.55 (3)","4.22 (3)","4.81 (3)","10.60 (3)","12.40 (3)"]
["Power input","Low","","","kW","0.018","0.032","0.057","0.047","0.064"]
["","High","","","kW","0.042","0.050","0.089","0.108","0.147"]
["Dimensions","Unit","","Height","mm","298","298","298","350","350"]
["","","","Width","mm","577","577","577","793","793"]
["","","","Depth","mm","577","577","577","793","793"]
["Weight","Unit","","","kg","23.0","23.0","23.0","43.0","43.0"]
["Decoration panel","Dimensions","Unit","Height","mm","41","41","41","75","75"]
["","","","Width","mm","730","730","730","860","860"]
["","","","Depth","mm","730","730","730","860","860"]
["Fan","Air flow rate","","Low","m³/h","289","306","479","718","902"]
["","","","High","m³/h","533","640","805","1,380","1,651"]
["Total sound power level","Low","","","dBA","33.0 (4)","40.0 (4)","47.0 (4)","35.0 (4)","40.0 (4)"]
["","High","","","dBA","45.0 (4)","50.0 (4)","58.0 (4)","51.0 (4)","56.0 (4)"]
["Sound pressure level","Low","","","dBA","25.0 (4)","32.0 (4)","39.0 (4)","27.0 (4)","32.0 (4)"]
["","High","","","dBA","37.0 (4)","42.0 (4)","50.0 (4)","43.0 (4)","48.0 (4)"]
["Water flow","Cooling","","Low","l/h","271 (1)","351 (1)","453 (1)","822 (1)","1,010 (1)"]
["","","","High","l/h","410 (1)","589 (1)","637 (1)","1,299 (1)","1,571 (1)"]
["","Heating","","High","l/h","311 (3)","369 (3)","421 (3)","929 (3)","1,083 (3)"]
["","","","Low","l/h","222 (3)","241 (3)","322 (3)","634 (3)","757 (3)"]
["","Water pressure drop","Cooling","Low","kPa","3 (1)","10 (1)","5 (1)","10 (1)","10 (1)"]
["","","","High","kPa","6 (1)","22 (1)","9 (1)","252 (1)","34 (1)"]
["","","Heating","Low","kPa","4 (3)","6 (3)","5 (3)","12 (3)","16 (3)"]
["","","","High","kPa","8 (3)","12 (3)","9 (3)","23 (3)","30 (3)"]
["Allowed water temperature","Cooling","","Min.","°C","5","5","5","5","5"]
["","Heating","","Max.","°C","80","80","80","80","80"]
["Piping connections","Water","","Inlet","","1/2\"","1/2\"","1/2\"","3/4\"","3/4\""]
["","","","Outlet","","1/2\"","1/2\"","1/2\"","3/4\"","3/4\""]
["","Drain","","OD","mm","10","10","10","10","10"]
["Water connections","Primary coil","","","inch","1/2\"","1/2\"","1/2\"","3/4\"","3/4\""]
["","Additional coil","","","inch","1/2\"","1/2\"","1/2\"","1/2\"","1/2\""]
["Control systems","Wired remote control","","","","FWEC1A, FWEC2A, FWEC3A, FWECSA, FWTOUCH","FWEC1A, FWEC2A, FWEC3A, FWECSA, FWTOUCH","FWEC1A, FWEC2A, FWEC3A, FWECSA, FWTOUCH","FWEC1A, FWEC2A, FWEC3A, FWECSA, FWTOUCH","FWEC1A, FWEC2A, FWEC3A, FWECSA, FWTOUCH"]
["Power supply","Type","","","","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50"]
["","Phase","","","","1~","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50","50"]
["","Voltage","","","V","230","230","230","230","230"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K."]
["","","","","","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K."]
["","","","","","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K."]
["","","","","","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741"]
["","","","","","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit."]