{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":51,"n_cols":11,"rows_kept":51,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWI-AT"]
[]
[]
[]
[]
["","","","","","FWI02AATN6V3","FWI03AATN6V3","FWI04AATN6V3","FWI07AATN6V3","FWI06AATN6V3","FWI08AATN6V3"]
["Cooling capacity (standard conditions)","Sensible capacity 2-pipe","","Low","kW","1.51 (1)","1.94 (1)","1.98 (1)","4.24 (1)","3.80 (1)","4.80 (1)"]
["","","","High","kW","2.20 (1)","3.41 (1)","4.11 (1)","6.78 (1)","4.75 (1)","7.97 (1)"]
["","Total capacity 2-pipe","","Low","kW","1.93 (1)","2.68 (1)","2.76 (1)","5.92 (1)","4.80 (1)","6.70 (1)"]
["","","","High","kW","2.63 (1)","4.39 (1)","5.23 (1)","9.04 (1)","6.39 (1)","10.50 (1)"]
["Heating capacity (standard conditions)","Capacity 2-pipe","","Low","kW","2.27 (2)","2.69 (2)","2.77 (2)","6.33 (2)","5.50 (2)","7.23 (2)"]
["","","","High","kW","3.25 (2)","4.58 (2)","5.55 (2)","10.20 (2)","7.30 (2)","12.20 (2)"]
["Power input","Low","","","kW","0.007","0.009","0.009","0.018","0.013","0.025"]
["","High","","","kW","0.018","0.037","0.067","0.067","0.036","0.150"]
["Dimensions","Unit","","Height","mm","298","298","298","350","350","350"]
["","","","Width","mm","577","577","577","793","793","793"]
["","","","Depth","mm","577","577","577","793","793","793"]
["Weight","Unit","","","kg","23.0","23.0","23.0","43.0","43.0","43.0"]
["Decoration panel","Dimensions","Unit","Height","mm","41","41","41","75","75","75"]
["","","","Width","mm","730","730","730","860","860","860"]
["","","","Depth","mm","730","730","730","860","860","860"]
["Fan","Air flow rate","","Low","m³/h","397","397","397","864","843","976"]
["","","","High","m³/h","583","796","980","1,554","1,276","1,831"]
["Total sound power level","Low","","","dBA","35.0 (4)","37.0 (4)","38.0 (4)","39.0 (4)","35.0 (4)","43.0 (4)"]
["","High","","","dBA","46.0 (4)","54.0 (4)","61.0 (4)","53.0 (4)","45.0 (4)","58.0 (4)"]
["Sound pressure level","Low","","","dBA","27.0 (4)","29.0 (4)","38.0 (4)","31.0 (4)","27.0 (4)","35.0 (4)"]
["","High","","","dBA","38.0 (4)","46.0 (4)","61.0 (4)","45.0 (4)","37.0 (4)","50.0 (4)"]
["Water flow","Cooling","","Low","l/h","331 (1)","460 (1)","473 (1)","1,015 (1)","833 (1)","1,150 (1)"]
["","","","High","l/h","452 (1)","754 (1)","898 (1)","1,545 (1)","1,097 (1)","1,805 (1)"]
["","Heating","","High","l/h","565 (2)","797 (2)","965 (2)","1,779 (2)","1,269 (2)","2,116 (2)"]
["","","","Low","l/h","395 (2)","468 (2)","482 (2)","1,100 (2)","953 (2)","1,257 (2)"]
["","Water pressure drop","Cooling","Low","kPa","4 (1)","10 (1)","9 (1)","12 (1)","12 (1)","15 (1)"]
["","","","High","kPa","7 (1)","23 (1)","29 (1)","29 (1)","21 (1)","36 (1)"]
["","","Heating","Low","kPa","5 (2)","8 (2)","8 (2)","12 (2)","13 (2)","15 (2)"]
["","","","High","kPa","9 (2)","21 (2)","27 (2)","29 (2)","23 (2)","36 (2)"]
["Allowed water temperature","Cooling","","Min.","°C","5","5","5","5","5","5"]
["","Heating","","Max.","°C","80","80","80","80","80","80"]
["Piping connections","Water","","Inlet","","1/2\"","1/2\"","1/2\"","3/4\"","3/4\"","3/4\""]
["","","","Outlet","","1/2\"","1/2\"","1/2\"","3/4\"","3/4\"","3/4\""]
["","Drain","","OD","mm","10","10","10","10","10","10"]
["Water connections","Primary coil","","","inch","1/2\"","1/2\"","1/2\"","3/4\"","3/4\"","3/4\""]
["Control systems","Wired remote control","","","","FWEC3A, FWECSA, FWTOUCH","FWEC3A, FWECSA, FWTOUCH","FWEC3A, FWECSA, FWTOUCH","FWEC3A, FWECSA, FWTOUCH","FWEC3A, FWECSA, FWTOUCH","FWEC3A, FWECSA, FWTOUCH"]
["Power supply","Type","","","","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50"]
["","Phase","","","","1~","1~","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50","50","50"]
["","Voltage","","","V","230","230","230","230","230","230"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K."]
["","","","","","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K."]
["","","","","","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K."]
["","","","","","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741"]
["","","","","","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit."]