{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":50,"n_cols":13,"rows_kept":50,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWP-CFN"]
[]
[]
[]
[]
["","","","","","FWP04CAFN6V3","FWP05CAFN6V3","FWP06CAFN6V3","FWP08CAFN6V3","FWP10CAFN6V3","FWP11CAFN6V3","FWP15CAFN6V3","FWP17CAFN6V3"]
["Sound pressure level","Low","","","dBA","20.0 (5)","31.0 (5)","31.0 (5)","30.0 (5)","30.0 (5)","30.0 (5)","53.0 (5)","53.0 (5)"]
["","High","","","dBA","44.0 (5)","46.0 (5)","46.0 (5)","50.0 (5)","50.0 (5)","50.0 (5)","61.0 (5)","61.0 (5)"]
["Total sound power level","Low","","","dBA","28.0 (4)","39.0 (4)","39.0 (4)","38.0 (4)","38.0 (4)","38.0 (4)","61.0 (4)","61.0 (4)"]
["","High","","","dBA","52.0 (4)","54.0 (4)","54.0 (4)","58.0 (4)","58.0 (4)","58.0 (4)","69.0 (4)","69.0 (4)"]
["Water flow","Cooling","","Low","l/h","161 (1)","221 (1)","274 (1)","339 (1)","394 (1)","432 (1)","1,094 (1)","1,225 (1)"]
["","","","High","l/h","333 (1)","404 (1)","522 (1)","656 (1)","822 (1)","925 (1)","1,295 (1)","1,448 (1)"]
["","Heating","","High","l/h","180 (3)","204 (3)","288 (3)","371 (3)","477 (3)","477 (3)","618 (3)","618 (3)"]
["","","","Low","l/h","100 (3)","136 (3)","183 (3)","245 (3)","297 (3)","297 (3)","592 (3)","592 (3)"]
["","Water pressure drop","Heating","High","kPa","3 (3)","3 (3)","4 (3)","6 (3)","14 (3)","14 (3)","22 (3)","22 (3)"]
["","","","Low","kPa","1 (3)","2 (3)","2 (3)","3 (3)","6 (3)","6 (3)","19 (3)","19 (3)"]
["","","Cooling","High","kPa","6 (1)","8 (1)","9 (1)","11 (1)","8 (1)","12 (1)","18 (1)","26 (1)"]
["","","","Low","kPa","2 (1)","3 (1)","3 (1)","3 (1)","2 (1)","3 (1)","13 (1)","20 (1)"]
["Piping connections","Drain","","OD","mm","17","17","17","17","17","17","17","17"]
["","Water","","Inlet","","1/2\"","1/2\"","1/2\"","1/2\"","3/4\"","3/4\"","3/4\"","3/4\""]
["","","","Outlet","","1/2\"","1/2\"","1/2\"","1/2\"","3/4\"","3/4\"","3/4\"","3/4\""]
["Power input","High","","","kW","0.032","0.039","0.035","0.077","0.067","0.067","0.162","0.162"]
["","Low","","","kW","0.006","0.010","0.010","0.021","0.011","0.011","0.105","0.105"]
["Allowed water temperature","Heating","","Max.","°C","80.000","80.000","80.000","80.000","80.000","80.000","80.000","80.000"]
["","Cooling","","Min.","°C","5","5","5","5","5","5","5","5"]
["Dimensions","Unit","","Width","mm","758","758","968","968","1,178","1,178","1,178","1,178"]
["","","","Depth","mm","665","665","665","665","745","745","745","745"]
["","","","Height","mm","250","250","250","250","280","280","280","280"]
["Water connections","Additional coil","","","inch","1/2\"","1/2\"","1/2\"","1/2\"","1/2\"","1/2\"","1/2\"","1/2\""]
["","Primary coil","","","inch","1/2\"","1/2\"","1/2\"","1/2\"","3/4 \"","3/4 \"","3/4 \"","3/4 \""]
["Weight","Unit","","","kg","25.8","26.8","34.6","37.6","47.5","47.5","53.5","53.5"]
["Fan","Air flow rate","","Low","m³/h","109","170","195","302","333","333","1,050","1,050"]
["","","","High","m³/h","270","336","398","642","755","755","1,289","1,289"]
["","Available static pressure","","High","Pa","63","77","63","75","61","61","60","60"]
["","","","Low","Pa","10","19","19","17","12","12","40","40"]
["Cooling capacity (standard conditions)","Total capacity 4-pipe","","Low","kW","0.93 (1)","1.28 (1)","1.59 (1)","1.95 (1)","2.29 (1)","2.51 (1)","6.28 (1)","7.04 (1)"]
["","","","High","kW","1.91 (1)","2.31 (1)","2.01 (1)","3.75 (1)","4.72 (1)","5.32 (1)","7.38 (1)","8.28 (1)"]
["","Sensible capacity 4-pipe","","Low","kW","0.62 (1)","0.90 (1)","1.09 (1)","1.47 (1)","1.67 (1)","1.77 (1)","4.64 (1)","4.96 (1)"]
["","","","High","kW","1.36 (1)","1.64 (1)","2.09 (1)","2.89 (1)","3.48 (1)","3.74 (1)","5.46 (1)","5.84 (1)"]
["Heating capacity (standard conditions)","Capacity 4-pipe","","Low","kW","1.14 (3)","1.55 (3)","2.09 (1)","2.80 (1)","3.40 (1)","3.40 (1)","6.42 (1)","6.42 (1)"]
["","","","High","kW","2.06 (3)","2.32 (3)","3.29 (1)","4.24 (1)","5.45 (1)","5.45 (1)","7.06 (1)","7.06 (1)"]
["Power supply","Type","","","","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50"]
["","Phase","","","","1~","1~","1~","1~","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","230","230","230","230","230","230","230","230"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K."]
["","","","","","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K."]
["","","","","","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K."]
["","","","","","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741"]
["","","","","","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit."]