{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":57,"n_cols":41,"rows_kept":57,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWQ-A"]
[]
[]
[]
[]
["","","","","","FWQ04AAFN5V1--","FWQ04AAFN5V1-R","FWQ04AATN5V1--","FWQ04AATN5V1-R","FWQ07AAFN5V1-R","FWQ07AATN5V1--","FWQ07AATN5V1-R","FWQ05AAFN5V1--","FWQ05AAFN5V1-R","FWQ05AATN5V1--","FWQ05AATN5V1-R","FWQ07AAFN5V1--","FWQ09AATN5V1-R","FWQ09AAFN5V1--","FWQ09AAFN5V1-R","FWQ09AATN5V1--","FWQ11AATN5V1-R","FWQ11AAFN5V1--","FWQ11AAFN5V1-R","FWQ11AATN5V1--","FWQ14AATN5V1--","FWQ14AATN5V1-R","FWQ14AAFN5V1--","FWQ14AAFN5V1-R","FWQ17AAFN5V1--","FWQ17AAFN5V1-R","FWQ17AATN5V1--","FWQ17AATN5V1-R","FWQ20AAFN5V1--","FWQ20AAFN5V1-R","FWQ20AATN5V1--","FWQ20AATN5V1-R","FWQ25AAFN5V1--","FWQ25AAFN5V1-R","FWQ25AATN5V1--","FWQ25AATN5V1-R"]
["Cooling capacity (standard conditions)","Sensible capacity 2-pipe","","Low","kW","","","1.07 (1)","1.07 (1)","","1.93 (1)","1.93 (1)","","","1.26 (1)","1.26 (1)","","2.50 (1)","","","2.50 (1)","3.36 (1)","","","3.36 (1)","4.26 (1)","4.26 (1)","","","","","5.05 (1)","5.05 (1)","","","5.33 (1)","5.33 (1)","","","6.30 (1)","6.30 (1)"]
["","","","High","kW","","","1.77 (1)","1.77 (1)","","2.80 (1)","2.80 (1)","","","2.08 (1)","2.08 (1)","","3.63 (1)","","","3.63 (1)","4.61 (1)","","","4.61 (1)","5.85 (1)","5.85 (1)","","","","","7.11 (1)","7.11 (1)","","","7.29 (1)","7.29 (1)","","","8.54 (1)","8.54 (1)"]
["","Sensible capacity 4-pipe","","Low","kW","0.98 (1)","0.98 (1)","","","1.76 (1)","","","1.18 (1)","1.18 (1)","","","1.76 (1)","","2.29 (1)","2.29 (1)","","","3.06 (1)","3.06 (1)","","","","3.89 (1)","3.89 (1)","4.62 (1)","4.62 (1)","","","4.90 (1)","4.90 (1)","","","5.74 (1)","5.74 (1)"]
["","","","High","kW","1.62 (1)","1.62 (1)","","","2.53 (1)","","","1.92 (1)","1.92 (1)","","","2.53 (1)","","3.30 (1)","3.30 (1)","","","4.18 (1)","4.18 (1)","","","","5.31 (1)","5.31 (1)","6.47 (1)","6.47 (1)","","","6.66 (1)","6.66 (1)","","","7.78 (1)","7.78 (1)"]
["","Total capacity 2-pipe","","Low","kW","","","1.46 (1)","1.46 (1)","","2.58 (1)","2.58 (1)","","","1.72 (1)","1.72 (1)","","3.30 (1)","","","3.30 (1)","4.40 (1)","","","4.40 (1)","5.59 (1)","5.59 (1)","","","","","6.53 (1)","6.53 (1)","","","7.80 (1)","7.80 (1)","","","9.19 (1)","9.19 (1)"]
["","","","High","kW","","","2.34 (1)","2.34 (1)","","3.64 (1)","3.64 (1)","","","2.73 (1)","2.73 (1)","","4.64 (1)","","","4.64 (1)","5.84 (1)","","","5.84 (1)","7.39 (1)","7.39 (1)","","","","","8.90 (1)","8.90 (1)","","","10.21 (1)","10.21 (1)","","","11.80 (1)","11.80 (1)"]
["","Total capacity 4-pipe","","Low","kW","1.31 (1)","1.31 (1)","","","2.31 (1)","","","1.55 (1)","1.55 (1)","","","2.31 (1)","","2.97 (1)","2.97 (1)","","","3.94 (1)","3.94 (1)","","","","5.02 (1)","5.02 (1)","5.88 (1)","5.88 (1)","","","7.05 (1)","7.05 (1)","","","8.21 (1)","8.21 (1)"]
["","","","High","kW","2.12 (1)","2.12 (1)","","","3.26 (1)","","","2.48 (1)","2.48 (1)","","","3.26 (1)","","4.18 (1)","4.18 (1)","","","5.23 (1)","5.23 (1)","","","","6.63 (1)","6.63 (1)","8.01 (1)","8.01 (1)","","","9.21 (1)","9.21 (1)","","","10.61 (1)","10.61 (1)"]
["Heating capacity (standard conditions)","Capacity 2-pipe","","Low","kW","","","1.59 (2)","1.59 (2)","","3.24 (2)","3.24 (2)","","","1.88 (2)","1.88 (2)","","3.80 (2)","","","3.80 (2)","4.95 (2)","","","4.95 (2)","6.13 (2)","6.13 (2)","","","","","6.61 (2)","6.61 (2)","","","7.89 (2)","7.89 (2)","","","9.21 (2)","9.21 (2)"]
["","","","High","kW","","","2.66 (2)","2.66 (2)","","4.01 (2)","4.01 (2)","","","3.13 (2)","3.13 (2)","","5.26 (2)","","","5.26 (2)","6.45 (2)","","","6.45 (2)","7.78 (2)","7.78 (2)","","","","","8.99 (2)","8.99 (2)","","","10.34 (2)","10.34 (2)","","","11.85 (2)","11.85 (2)"]
["","Capacity 4-pipe","","Low","kW","1.64 (3)","1.64 (3)","","","2.73 (3)","","","1.94 (3)","1.94 (3)","","","2.73 (3)","","3.31 (3)","3.31 (3)","","","4.32 (3)","4.32 (3)","","","","5.37 (3)","5.37 (3)","5.83 (3)","5.83 (3)","","","6.96 (3)","6.96 (3)","","","8.05 (3)","8.05 (3)"]
["","","","High","kW","2.54 (3)","2.54 (3)","","","3.56 (3)","","","2.93 (3)","2.93 (3)","","","3.56 (3)","","4.56 (3)","4.56 (3)","","","5.61 (3)","5.61 (3)","","","","6.75 (3)","6.75 (3)","7.92 (3)","7.92 (3)","","","9.10 (3)","9.10 (3)","","","10.41 (3)","10.41 (3)"]
["Power input","Low","","","kW","0.03 (4)","0.03 (4)","0.03 (4)","0.03 (4)","0.04 (4)","0.04 (4)","0.04 (4)","0.04 (4)","0.04 (4)","0.04 (4)","0.04 (4)","0.04 (4)","0.05 (4)","0.05 (4)","0.05 (4)","0.05 (4)","0.06 (4)","0.06 (4)","0.06 (4)","0.06 (4)","0.06 (4)","0.06 (4)","0.06 (4)","0.06 (4)","0.09 (4)","0.09 (4)","0.09 (4)","0.09 (4)","0.10 (4)","0.10 (4)","0.10 (4)","0.10 (4)","0.11 (4)","0.11 (4)","0.11 (4)","0.11 (4)"]
["","High","","","kW","0.045 (4)","0.045 (4)","0.045 (4)","0.045 (4)","0.069 (4)","0.069 (4)","0.069 (4)","0.056 (4)","0.056 (4)","0.056 (4)","0.056 (4)","0.069 (4)","0.072 (4)","0.072 (4)","0.072 (4)","0.072 (4)","0.126 (4)","0.126 (4)","0.126 (4)","0.126 (4)","0.149 (4)","0.149 (4)","0.149 (4)","0.149 (4)","0.152 (4)","0.152 (4)","0.152 (4)","0.152 (4)","0.160 (4)","0.160 (4)","0.160 (4)","0.160 (4)","0.200 (4)","0.200 (4)","0.200 (4)","0.200 (4)"]
["Dimensions","Unit","","Height","mm","249","249","249","249","249","249","249","249","249","249","249","249","249","249","249","249","249","249","249","249","249","249","249","249","249","249","249","249","249","249","249","249","249","249","249","249"]
["","","","Width","mm","592","592","592","592","742","742","742","592","592","592","592","742","1100","1100","1100","1100","1100","1100","1100","1100","1100","1100","1100","1100","1520","1520","1520","1520","1520","1520","1520","1520","1520","1520","1520","1520"]
["","","","Depth","mm","793","793","793","793","793","793","793","793","793","793","793","793","793","793","793","793","793","793","793","793","793","793","793","793","793","793","793","793","793","793","793","793","793","793","793","793"]
["Weight","Unit","","","kg","27.0","27.0","26.0","26.0","32.0","30.0","30.0","27.0","27.0","26.0","26.0","32.0","40.0","43.0","43.0","40.0","40.0","43.0","43.0","40.0","40.0","40.0","43.0","43.0","55.0","55.0","52.0","52.0","55.0","55.0","52.0","52.0","55.0","55.0","52.0","52.0"]
["Casing","Colour","","","","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal"]
["Fan","Air flow rate","","Low","m³/h","223 (4)","223 (4)","246 (4)","246 (4)","436 (4)","480 (4)","480 (4)","269 (4)","269 (4)","296 (4)","296 (4)","436 (4)","598 (4)","544 (4)","544 (4)","598 (4)","822 (4)","747 (4)","747 (4)","822 (4)","1091 (4)","1091 (4)","992 (4)","992 (4)","996 (4)","996 (4)","1096 (4)","1096 (4)","1228 (4)","1228 (4)","1351 (4)","1351 (4)","1472 (4)","1472 (4)","1636 (4)","1636 (4)"]
["","","","High","m³/h","390 (4)","390 (4)","429 (4)","429 (4)","646 (4)","711 (4)","711 (4)","470 (4)","470 (4)","517 (4)","517 (4)","646 (4)","887 (4)","806 (4)","806 (4)","887 (4)","1176 (4)","1069 (4)","1069 (4)","1176 (4)","1612 (4)","1612 (4)","1465 (4)","1465 (4)","1443 (4)","1443 (4)","1587 (4)","1587 (4)","1730 (4)","1730 (4)","1903 (4)","1903 (4)","2100 (4)","2100 (4)","2310 (4)","2310 (4)"]
["","Available static pressure","","Low","Pa","20","20","20","20","26","26","26","20","20","20","20","26","26","26","26","26","26","26","26","26","26","26","26","26","26","26","26","26","26","26","26","26","26","26","26","26"]
["","","","High","Pa","60","60","60","60","60","60","60","60","60","60","60","60","60","60","60","60","60","60","60","60","60","60","60","60","60","60","60","60","60","60","60","60","60","60","60","60"]
["Total sound power level","Low","","","dBA","43.0 (5)","43.0 (5)","44.0 (5)","44.0 (5)","49.0 (5)","50.0 (5)","50.0 (5)","45.0 (5)","45.0 (5)","46.0 (5)","46.0 (5)","49.0 (5)","50.0 (5)","49.0 (5)","49.0 (5)","50.0 (5)","51.0 (5)","50.0 (5)","50.0 (5)","51.0 (5)","57.0 (5)","57.0 (5)","56.0 (5)","56.0 (5)","52.0 (5)","52.0 (5)","53.0 (5)","53.0 (5)","53.0 (5)","53.0 (5)","54.0 (5)","54.0 (5)","55.0 (5)","55.0 (5)","56.0 (5)","56.0 (5)"]
["","High","","","dBA","51.0 (5)","51.0 (5)","52.0 (5)","52.0 (5)","58.0 (5)","59.0 (5)","59.0 (5)","54.0 (5)","54.0 (5)","55.0 (5)","55.0 (5)","58.0 (5)","57.0 (5)","56.0 (5)","56.0 (5)","57.0 (5)","58.0 (5)","57.0 (5)","57.0 (5)","58.0 (5)","63.0 (5)","63.0 (5)","62.0 (5)","62.0 (5)","60.0 (5)","60.0 (5)","61.0 (5)","61.0 (5)","60.0 (5)","60.0 (5)","61.0 (5)","61.0 (5)","61.0 (5)","61.0 (5)","62.0 (5)","62.0 (5)"]
["Sound pressure level","Low","","","dBA","27.0 (6)","27.0 (6)","28.0 (6)","28.0 (6)","33.0 (6)","34.0 (6)","34.0 (6)","29.0 (6)","29.0 (6)","30.0 (6)","30.0 (6)","33.0 (6)","34.0 (6)","33.0 (6)","33.0 (6)","34.0 (6)","35.0 (6)","34.0 (6)","34.0 (6)","35.0 (6)","41.0 (6)","41.0 (6)","40.0 (6)","40.0 (6)","36.0 (6)","36.0 (6)","37.0 (6)","37.0 (6)","37.0 (6)","37.0 (6)","38.0 (6)","38.0 (6)","39.0 (6)","39.0 (6)","40.0 (6)","40.0 (6)"]
["","High","","","dBA","35.0 (6)","35.0 (6)","36.0 (6)","36.0 (6)","42.0 (6)","43.0 (6)","43.0 (6)","38.0 (6)","38.0 (6)","39.0 (6)","39.0 (6)","42.0 (6)","41.0 (6)","40.0 (6)","40.0 (6)","41.0 (6)","42.0 (6)","41.0 (6)","41.0 (6)","42.0 (6)","47.0 (6)","47.0 (6)","46.0 (6)","46.0 (6)","44.0 (6)","44.0 (6)","45.0 (6)","45.0 (6)","44.0 (6)","44.0 (6)","45.0 (6)","45.0 (6)","45.0 (6)","45.0 (6)","46.0 (6)","46.0 (6)"]
["Water flow","Cooling","","Low","l/h","225 (1)","225 (1)","250 (1)","250 (1)","398 (1)","444 (1)","444 (1)","266 (1)","266 (1)","296 (1)","296 (1)","398 (1)","568 (1)","511 (1)","511 (1)","568 (1)","757 (1)","678 (1)","678 (1)","757 (1)","961 (1)","961 (1)","862 (1)","862 (1)","1011 (1)","1011 (1)","1123 (1)","1123 (1)","1212 (1)","1212 (1)","1342 (1)","1342 (1)","1412 (1)","1412 (1)","1580 (1)","1580 (1)"]
["","","","High","l/h","365 (1)","365 (1)","402 (1)","402 (1)","561 (1)","626 (1)","626 (1)","426 (1)","426 (1)","469 (1)","469 (1)","561 (1)","799 (1)","719 (1)","719 (1)","799 (1)","1005 (1)","900 (1)","900 (1)","1005 (1)","1271 (1)","1271 (1)","1140 (1)","1140 (1)","1377 (1)","1377 (1)","1530 (1)","1530 (1)","1585 (1)","1585 (1)","1756 (1)","1756 (1)","1825 (1)","1825 (1)","2029 (1)","2029 (1)"]
["","Heating","","Low","l/h","141 (3)","141 (3)","273 (2)","273 (2)","234 (3)","557 (2)","557 (2)","167 (3)","167 (3)","323 (2)","323 (2)","234 (3)","654 (2)","285 (3)","285 (3)","654 (2)","851 (2)","371 (3)","371 (3)","851 (2)","1054 (2)","1054 (2)","461 (3)","461 (3)","501 (3)","501 (3)","1136 (2)","1136 (2)","598 (3)","598 (3)","1356 (2)","1356 (2)","692 (3)","692 (3)","1583 (2)","1583 (2)"]
["","","","High","l/h","219 (3)","219 (3)","457 (2)","457 (2)","306 (3)","690 (2)","690 (2)","252 (3)","252 (3)","539 (2)","539 (2)","306 (3)","904 (2)","392 (3)","392 (3)","904 (2)","1109 (2)","482 (3)","482 (3)","1109 (2)","1337 (2)","1337 (2)","581 (3)","581 (3)","681 (3)","681 (3)","1546 (2)","1546 (2)","782 (3)","782 (3)","1777 (2)","1777 (2)","895 (3)","895 (3)","2038 (2)","2038 (2)"]
["","Water pressure drop","Cooling","Low","kPa","6 (1)","6 (1)","8 (1)","8 (1)","7 (1)","9 (1)","9 (1)","9 (1)","9 (1)","10 (1)","10 (1)","7 (1)","5 (1)","4 (1)","4 (1)","5 (1)","9 (1)","7 (1)","7 (1)","9 (1)","14 (1)","14 (1)","11 (1)","11 (1)","17 (1)","17 (1)","20 (1)","20 (1)","24 (1)","24 (1)","28 (1)","28 (1)","32 (1)","32 (1)","38 (1)","38 (1)"]
["","","","High","kPa","14 (1)","14 (1)","16 (1)","16 (1)","13 (1)","16 (1)","16 (1)","18 (1)","18 (1)","21 (1)","21 (1)","13 (1)","9 (1)","8 (1)","8 (1)","9 (1)","14 (1)","12 (1)","12 (1)","14 (1)","22 (1)","22 (1)","18 (1)","18 (1)","29 (1)","29 (1)","35 (1)","35 (1)","38 (1)","38 (1)","46 (1)","46 (1)","50 (1)","50 (1)","60 (1)","60 (1)"]
["","","Heating","Low","kPa","3 (3)","3 (3)","9 (2)","9 (2)","8 (3)","13 (2)","13 (2)","4 (3)","4 (3)","12 (2)","12 (2)","8 (3)","7 (2)","9 (3)","9 (3)","7 (2)","11 (2)","10 (3)","10 (3)","11 (2)","16 (2)","16 (2)","12 (3)","12 (3)","12 (3)","12 (3)","21 (2)","21 (2)","17 (3)","17 (3)","29 (2)","29 (2)","22 (3)","22 (3)","39 (2)","39 (2)"]
["","","","High","kPa","6 (3)","6 (3)","20 (2)","20 (2)","12 (3)","19 (2)","19 (2)","8 (3)","8 (3)","27 (2)","27 (2)","12 (3)","11 (2)","13 (3)","13 (3)","11 (2)","17 (2)","15 (3)","15 (3)","17 (2)","24 (2)","24 (2)","19 (3)","19 (3)","22 (3)","22 (3)","36 (2)","36 (2)","29 (3)","29 (3)","47 (2)","47 (2)","37 (3)","37 (3)","61 (2)","61 (2)"]
["Allowed water temperature","Cooling","","Min.","°C","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5","5"]
["","","","Max.","°C","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0","90.0"]
["","Heating","","Min.","°C","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00","5.00"]
["","","","Max.","°C","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000","90.000"]
["Piping connections","Water","","Inlet","","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)"]
["","","","Outlet","","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)"]
["Power supply","Type","","","","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50"]
["","Phase","","","","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240"]
["Notes","","","","","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB.","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB."]
["","","","","","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K for two pipe model."]
["","","","","","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K for four pipe model."]
["","","","","","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741.","(4) - Sound power level according to ISO3741."]
["","","","","","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The discharge sound pressure level is measured via a microphone at 1m distance of the unit."]
["","","","","","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings.","(6) - The available static pressure value corresponds to the default factory DIP Switch settings."]