{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":49,"n_cols":10,"rows_kept":49,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWT-GT"]
[]
[]
[]
[]
["","","","","","FWT02GATNMV1","FWT03GATNMV1","FWT04GATNMV1","FWT05GATNMV1","FWT06GATNMV1"]
["Cooling capacity (standard conditions)","Sensible capacity 2-pipe","","Low","kW","1.50 (1)","1.49 (1)","1.91 (1)","2.77 (1)","3.22 (1)"]
["","","","High","kW","1.82 (1)","1.99 (1)","2.60 (1)","3.38 (1)","4.03 (1)"]
["","Total capacity 2-pipe","","Low","kW","1.94 (1)","2.02 (1)","2.52 (1)","3.76 (1)","4.04 (1)"]
["","","","High","kW","2.40 (1)","2.67 (1)","3.27 (1)","4.49 (1)","5.21 (1)"]
["Heating capacity (standard conditions)","Capacity 2-pipe","","Low","kW","2.06 (2)","2.25 (2)","2.75 (2)","4.03 (2)","4.83 (2)"]
["","","","High","kW","2.71 (2)","2.96 (2)","3.71 (2)","5.07 (2)","6.23 (2)"]
["Power input","Low","","","kW","0.03","0.03","0.03","0.04","0.06"]
["","High","","","kW","0.031","0.032","0.042","0.053","0.072"]
["Dimensions","Unit","","Height","mm","288","288","288","310","310"]
["","","","Width","mm","800","800","800","1,070","1,070"]
["","","","Depth","mm","206","206","206","224","224"]
["Weight","Unit","","","kg","9.00","9.00","9.00","14.0","14.0"]
["Casing","Colour","","","","White","White","White","White","White"]
["Fan","Air flow rate","","Low","m³/h","340 (3)","374 (3)","442 (3)","663 (3)","782 (3)"]
["","","","High","m³/h","442 (3)","476 (3)","629 (3)","866 (3)","1,053 (3)"]
["Total sound power level","Low","","","dBA","36 (4)","39 (4)","45 (4)","47 (4)","51 (4)"]
["","High","","","dBA","45 (4)","48 (4)","55 (4)","55 (4)","59 (4)"]
["Sound pressure level","Low","","","dBA","25 (5)","25 (5)","32 (5)","34 (5)","39 (5)"]
["","High","","","dBA","34 (5)","35 (5)","42 (5)","42 (5)","46 (5)"]
["Water flow","Cooling","","Low","l/h","420","460","570","780","910"]
["","","","High","l/h","420","460","570","780","910"]
["","Heating","","High","l/h","420","460","570","780","910"]
["","","","Low","l/h","420","460","570","780","910"]
["","Water pressure drop","Cooling","Low","kPa","24","20","28","23","26"]
["","","","High","kPa","34","24","31","30","36"]
["","","Heating","Low","kPa","23","16","19","24","30"]
["","","","High","kPa","35","23","31","32","42"]
["Piping connections","Water","","Inlet","","1/2\"","1/2\"","1/2\"","1/2\"","1/2\""]
["","","","Outlet","","1/2\"","1/2\"","1/2\"","1/2\"","1/2\""]
["","Drain","","OD","mm","19","19","19","19","19"]
["Power supply","Type","","","","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50"]
["","Phase","","","","1N~","1N~","1N~","1N~","1N~"]
["","Frequency","","","Hz","50","50","50","50","50"]
["","Voltage","","","V","220-240","220-240","220-240","220-240","220-240"]
["Current input","Low","","","A","0.17","0.19","0.19","0.25","0.31"]
["","High","","","A","0.19","0.20","0.21","0.29","0.34"]
["Fan motor","Power input","","Low","kW","0.025","0.029","0.033","0.042","0.060"]
["","","","High","kW","0.031","0.032","0.042","0.053","0.072"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K."]
["","","","","","(2) - Heating: 2 pipe: air 20°CDB; entering water 50°C","(2) - Heating: 2 pipe: air 20°CDB; entering water 50°C","(2) - Heating: 2 pipe: air 20°CDB; entering water 50°C","(2) - Heating: 2 pipe: air 20°CDB; entering water 50°C","(2) - Heating: 2 pipe: air 20°CDB; entering water 50°C"]
["","","","","","(3) - Air flow at 0Pa ESP","(3) - Air flow at 0Pa ESP","(3) - Air flow at 0Pa ESP","(3) - Air flow at 0Pa ESP","(3) - Air flow at 0Pa ESP"]
["","","","","","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741"]
["","","","","","(5) - Sound pressure measured at 1m in front of the unit and 0.8m below the vertical centre line of the unit (JIS C 9612).","(5) - Sound pressure measured at 1m in front of the unit and 0.8m below the vertical centre line of the unit (JIS C 9612).","(5) - Sound pressure measured at 1m in front of the unit and 0.8m below the vertical centre line of the unit (JIS C 9612).","(5) - Sound pressure measured at 1m in front of the unit and 0.8m below the vertical centre line of the unit (JIS C 9612).","(5) - Sound pressure measured at 1m in front of the unit and 0.8m below the vertical centre line of the unit (JIS C 9612)."]