{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":44,"n_cols":9,"rows_kept":44,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWZ-AT"]
[]
[]
[]
[]
["","","","","","FWZ02AATV3","FWZ03AATV3","FWZ06AATV3","FWZ08AATV3"]
["Sound pressure level","Low","","","dBA","35 (6)","31 (6)","38 (6)","44 (5)"]
["","High","","","dBA","45 (6)","43 (6)","51 (6)","62 (5)"]
["Total sound power level","Low","","","dBA","40 (4)","36 (4)","43 (4)","49 (4)"]
["","High","","","dBA","50 (4)","48 (4)","56 (4)","67 (4)"]
["Water flow","Cooling","","Low","l/h","234 (1)","302 (1)","515 (1)","706 (1)"]
["","","","High","l/h","337 (1)","503 (1)","774 (1)","1,376 (1)"]
["","Heating","","High","l/h","373 (2)","506 (2)","866 (2)","1,455 (2)"]
["","","","Low","l/h","260 (2)","301 (2)","575 (2)","764 (2)"]
["","Water pressure drop","Heating","High","kPa","12 (2)","11 (2)","14 (2)","18 (2)"]
["","","","Low","kPa","6 (2)","5 (2)","7 (2)","6 (2)"]
["","","Cooling","High","kPa","12 (1)","11 (1)","14 (1)","20 (1)"]
["","","","Low","kPa","6 (1)","5 (1)","7 (1)","6 (1)"]
["Piping connections","Drain","","OD","mm","16","16","16","16"]
["Power input","High","","","kW","0.019","0.016","0.033","0.087"]
["","Low","","","kW","0.01","0.01","0.01","0.013"]
["Dimensions","Unit","","Width","mm","774","984","1,190","1,404"]
["","","","Depth","mm","226","226","226","251"]
["","","","Height","mm","564","564","564","564"]
["Water connections","Additional coil","","","inch","","1/2\""]
["","Primary coil","","","inch","1/2\"","1/2\"","1/2\"","3/4 \""]
["Casing","Colour","","","","White - RAL9010","White - RAL9010","White - RAL9010"]
["Weight","Unit","","","kg","20.6","26.7","32.3","41.6"]
["Cooling capacity (standard conditions)","Sensible capacity 2-pipe","","Low","kW","1.04 (1)","1.25 (1)","2.31 (1)","3.04 (1)"]
["","","","High","kW","1.49 (1)","2.09 (1)","3.62 (1)","5.87 (1)"]
["","Total capacity 2-pipe","","Low","kW","1.35 (1)","1.75 (1)","2.99 (1)","4.10 (1)"]
["","","","High","kW","1.94 (1)","2.91 (1)","4.48 (1)","7.93 (1)"]
["Heating capacity (standard conditions)","Capacity 2-pipe","","High","kW","2.15 (2)","2.94 (2)","4.88 (2)","8.37 (2)"]
["","","","Low","kW","1.50 (2)","1.76 (2)","3.36 (2)","4.39 (2)"]
["Power supply","Type","","","","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50"]
["","Phase","","","","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50"]
["","Voltage","","","V","230","230","230","230"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K."]
["","","","","","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K."]
["","","","","","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K."]
["","","","","","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741"]
["","","","","","(5) - SL: The silent fan level of the air flow rate setting","(5) - SL: The silent fan level of the air flow rate setting","(5) - SL: The silent fan level of the air flow rate setting","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit."]
["","","","","","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit."]