{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":47,"n_cols":8,"rows_kept":47,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FXAQ-PVER"]
[]
[]
[]
[]
["","","","","","FXAQ40PVER1","FXAQ50PVER1","FXAQ63PVER1"]
["Sound pressure level","Heating","","At high fan speed","dBA","39.0","42.0","47.0"]
["","","","At low fan speed","dBA","34.0","37.0","41.0"]
["","Cooling","","At low fan speed","dBA","34.0","37.0","41.0"]
["","","","At high fan speed","dBA","39.0","42.0","47.0"]
["Standard Accessories","Operation manual","","","","Operation manual","Operation manual","Operation manual"]
["","Installation manual","","","","Installation manual","Installation manual","Installation manual"]
["","Installation panel","","","","Installation panel","Installation panel","Installation panel"]
["","Paper pattern for installation","","","","Paper pattern for installation","Paper pattern for installation","Paper pattern for installation"]
["","Insulation tape","","","","Insulation tape","Insulation tape","Insulation tape"]
["","Clamps","","","","Clamps","Clamps","Clamps"]
["","Screws","","","","Screws","Screws","Screws"]
["Refrigerant","GWP","","","","2,087.5","2,087.5","2,087.5"]
["","Type","","","","R-410A","R-410A","R-410A"]
["System","Connectable outdoor unit system","","","","R410A VRV Series","R410A VRV Series","R410A VRV Series"]
["Power input - 50Hz","Cooling","","At high fan speed","kW","0.020 (1)","0.033 (1)","0.050 (1)"]
["","Heating","","At high fan speed","kW","0.020 (2)","0.039 (2)","0.060 (2)"]
["Cooling capacity","Total capacity","","At high fan speed","kW","4.5 (1)","5.6 (1)","7.1 (1)"]
["Piping connections","Liquid","","OD","mm","6.35","6.35","9.52"]
["","","","Type","","Flare connection","Flare connection","Flare connection"]
["","Gas","","OD","mm","12.7","12.7","15.9"]
["","","","Type","","Flare connection","Flare connection","Flare connection"]
["","Drain","","","","VP13 (I.D. 13/O.D. 18)","VP13 (I.D. 13/O.D. 18)","VP13 (I.D. 13/O.D. 18)"]
["Air filter","Type","","","","Washable resin net","Washable resin net","Washable resin net"]
["Dimensions","Unit","","Width","mm","1,050","1,050","1,050"]
["","","","Depth","mm","238","238","238"]
["","","","Height","mm","290","290","290"]
["Casing","Colour","","","","White (3.0Y8.5/0.5)","White (3.0Y8.5/0.5)","White (3.0Y8.5/0.5)"]
["Weight","Unit","","","kg","14","14","14"]
["Fan","Air flow rate - 50Hz","Cooling","At high fan speed","m³/min","12","15","19"]
["","","","At low fan speed","m³/min","9","12","14"]
["","Air flow rate - 60Hz","Cooling","High","m³/min","12","15","19"]
["","","","Low","m³/min","9","12","14"]
["Heating capacity","Total capacity","","At high fan speed","kW","5.0 (2)","6.3 (2)","8.0 (2)"]
["Current - 50Hz","Maximum fuse amps (MFA)","","","A","15","15","15"]
["Power supply","Phase","","","","1~","1~","1~"]
["","Frequency","","","Hz","50/60","50/60","50/60"]
["","Voltage","","","V","220-240/220","220-240/220","220-240/220"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)"]
["","","","","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)"]
["","","","","","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat."]
["","","","","","(4) - Contains fluorinated greenhouse gases","(4) - Contains fluorinated greenhouse gases","(4) - Contains fluorinated greenhouse gases"]