{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":72,"n_cols":8,"rows_kept":72,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FXFN-A2"]
[]
[]
[]
[]
["","","","","","FXFN50A2VEB","FXFN71A2VEB","FXFN112A2VEB"]
["Sound pressure level","Heating","","At high fan speed","dBA","36.0","41.0","47.0"]
["","","","At low fan speed","dBA","31.0","33.0","39.0"]
["","","","At medium fan speed","dBA","34.0","37.0","44.0"]
["","Cooling","","At low fan speed","dBA","31.0","33.0","38.0"]
["","","","At high fan speed","dBA","35.0","40.0","46.0"]
["","","","At medium fan speed","dBA","33.0","36.0","43.0"]
["Standard Accessories","Installation and operation manual","","","","1","1","1"]
["","Drain hose","","","","1","1","1"]
["","Clamp for drain hose","","","","1","1","1"]
["","Washer for hanger bracket","","","","8","8","8"]
["","Screws","","","","4","4","4"]
["","Installation guide","","","","1","1","1"]
["","Insulation for fitting","","","","2","2","2"]
["","Sealing pads","","","","1","1","1"]
["","Wire clamp material","","","","7","7","7"]
["","Clamps","","","","1","1","1"]
["Refrigerant","GWP","","","","1","1","1"]
["","Type","","","","R744 (CO2)","R744 (CO2)","R744 (CO2)"]
["Power input - 50Hz","Cooling","","At high fan speed","kW","0.019","0.046","0.096"]
["","Heating","","At high fan speed","kW","0.019","0.046","0.096"]
["Cooling capacity","Total capacity","","At high fan speed","kW","5.60","8.00","12.50"]
["Piping connections","Liquid","","OD","mm","9.52","9.52","9.52"]
["","","","Type","","Braze connection","Braze connection","Braze connection"]
["","Gas","","OD","mm","12.70","12.70","12.70"]
["","","","Type","","Braze connection","Braze connection","Braze connection"]
["","Drain","","","","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)"]
["Sound power level","Cooling","","At high fan speed","dBA","53.0","58.0","63.0"]
["Air filter","Type","","","","Resin net","Resin net","Resin net"]
["Dimensions","Unit","","Width","mm","840","840","840"]
["","","","Depth","mm","840","840","840"]
["","","","Height","mm","246","246","288"]
["Casing","Material","","","","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate"]
["Weight","Unit","","","kg","26","26","29"]
["Decoration panel 2","Weight","","","kg","10.3","10.3","10.3"]
["","Model","","","","BYCQ140E2GFW1, BYCQ140E2GFW1B","BYCQ140E2GFW1, BYCQ140E2GFW1B","BYCQ140E2GFW1, BYCQ140E2GFW1B"]
["","Dimensions","","Depth","mm","950","950","950"]
["","","","Width","mm","950","950","950"]
["","","","Height","mm","148","148","148"]
["Decoration panel 3","Dimensions","","Depth","mm","950","950","950"]
["","","","Height","mm","106","106","106"]
["","","","Width","mm","950","950","950"]
["","Model","","","","BYCQ140E2P, BYCQ140E2PB","BYCQ140E2P, BYCQ140E2PB","BYCQ140E2P, BYCQ140E2PB"]
["","Weight","","","kg","6.5","6.5","6.5"]
["Fan","Air flow rate - 50Hz","Cooling","At high fan speed","m³/min","15.5","23.2","32.7"]
["","","","At low fan speed","m³/min","10.7","13.8","20.6"]
["Decoration panel","Weight","","","kg","5.5","5.5","5.5"]
["","Model","","","","BYCQ140E2W1, BYCQ140E2W1W, BYCQ140E2W1B","BYCQ140E2W1, BYCQ140E2W1W, BYCQ140E2W1B","BYCQ140E2W1, BYCQ140E2W1W, BYCQ140E2W1B"]
["","Dimensions","","Height","mm","65","65","65"]
["","","","Depth","mm","950","950","950"]
["","","","Width","mm","950","950","950"]
["Heating capacity","Total capacity","","At high fan speed","kW","6.30","9.00","14.00"]
["Current - 50Hz","Maximum fuse amps (MFA)","","","A","6","6","6"]
["Power supply","Phase","","","","1~","1~","1~"]
["","Frequency","","","Hz","50/60","50/60","50/60"]
["","Voltage","","","V","220-240/220","220-240/220","220-240/220"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19.0°CWB; outdoor temp. 35°CDB","(1) - Cooling: indoor temp. 27°CDB, 19.0°CWB; outdoor temp. 35°CDB","(1) - Cooling: indoor temp. 27°CDB, 19.0°CWB; outdoor temp. 35°CDB"]
["","","","","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB"]
["","","","","","(3) - The sound power level is an absolute value indicating the power which a sound source generates.","(3) - The sound power level is an absolute value indicating the power which a sound source generates.","(3) - The sound power level is an absolute value indicating the power which a sound source generates."]
["","","","","","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(6) - MCA/MFA: MCA = 1.1 x FLA","(6) - MCA/MFA: MCA = 1.1 x FLA","(6) - MCA/MFA: MCA = 1.1 x FLA"]
["","","","","","(7) - Instead of a fuse, use a circuit breaker","(7) - Instead of a fuse, use a circuit breaker","(7) - Instead of a fuse, use a circuit breaker"]
["","","","","","(8) - Select wire size based on the value of MCA","(8) - Select wire size based on the value of MCA","(8) - Select wire size based on the value of MCA"]
["","","","","","(9) - BYCQ140E2W1: pure white standard panel with grey louvers; BYCQ140E2W1W: pure white standard panel with white louvers; BYCQ140E2W1B: black standard panel with black louvers.","(9) - BYCQ140E2W1: pure white standard panel with grey louvers; BYCQ140E2W1W: pure white standard panel with white louvers; BYCQ140E2W1B: black standard panel with black louvers.","(9) - BYCQ140E2W1: pure white standard panel with grey louvers; BYCQ140E2W1W: pure white standard panel with white louvers; BYCQ140E2W1B: black standard panel with black louvers."]
["","","","","","(10) - The BYCQ140E2W1W has white insulations. Be informed that formation of dirt on white insulation is visibly stronger and that it is consequently not advised to install the BYCQ140E2W1W decoration panel in enviroments exposed to concentrations of dirt.","(10) - The BYCQ140E2W1W has white insulations. Be informed that formation of dirt on white insulation is visibly stronger and that it is consequently not advised to install the BYCQ140E2W1W decoration panel in enviroments exposed to concentrations of dirt.","(10) - The BYCQ140E2W1W has white insulations. Be informed that formation of dirt on white insulation is visibly stronger and that it is consequently not advised to install the BYCQ140E2W1W decoration panel in enviroments exposed to concentrations of dirt."]
["","","","","","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases"]