{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":56,"n_cols":11,"rows_kept":56,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FXKQ-A"]
[]
[]
[]
[]
["","","","","","FXKQ20AMVEB","FXKQ25AMVEB","FXKQ32AMVEB","FXKQ40AMVEB","FXKQ50AMVEB","FXKQ63AMVEB"]
["Cooling capacity","Total capacity","","At high fan speed","kW","2.2","2.8","3.6","4.5","5.6","7.1"]
["Heating capacity","Total capacity","","At high fan speed","kW","2.5","3.2","4","5","6.3","8"]
["Power input - 50Hz","Cooling","","At high fan speed","kW","0.026","0.026","0.039","0.047","0.073","0.118"]
["","Heating","","At high fan speed","kW","0.034","0.034","0.039","0.047","0.073","0.118"]
["Dimensions","Unit","","Height","mm","200","200","200","200","200","200"]
["","","","Width","mm","840","840","840","1240","1240","1240"]
["","","","Depth","mm","470","470","470","470","470","470"]
["Weight","Unit","","","kg","18","18","19","24","24","24"]
["Casing","Colour","","","","Not painted (galvanised)","Not painted (galvanised)","Not painted (galvanised)","Not painted (galvanised)","Not painted (galvanised)","Not painted (galvanised)"]
["","Material","","","","Galvanised steel","Galvanised steel","Galvanised steel","Galvanised steel","Galvanised steel","Galvanised steel"]
["Fan","Air flow rate - 50Hz","Cooling","At high fan speed","m³/min","7.5","7.5","9.4","14.4","17.6","21.5"]
["","","","At low fan speed","m³/min","5","5","7.6","11.1","12.6","14.4"]
["Refrigerant","Type","","","","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A"]
["","GWP","","","","2087.5","2087.5","2087.5","2087.5","2087.5","2087.5"]
["Sound power level","Cooling","","At high fan speed","dBA","46","46","50.5","52.5","57","61.5"]
["Sound pressure level","Cooling","","At high fan speed","dBA","32","32","37","38.5","42","48.5"]
["","","","At medium fan speed","dBA","27.5","27.5","34","34.5","38","43.5"]
["","","","At low fan speed","dBA","22.5","22.5","31.5","31.5","34.5","38.5"]
["","Heating","","At high fan speed","dBA","36","36","39","39.5","44","49"]
["","","","At medium fan speed","dBA","31","31","35.5","36","39.5","44"]
["","","","At low fan speed","dBA","25.5","25.5","32.5","32.5","36","39.5"]
["Piping connections","Liquid","","Type","","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection"]
["","","","OD","mm","6.4","6.4","6.4","6.4","6.4","9.5"]
["","Gas","","Type","","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection"]
["","","","OD","mm","12.7","12.7","12.7","12.7","12.7","15.9"]
["","Drain","","","","I.D. 20/O.D. 26","I.D. 20/O.D. 26","I.D. 20/O.D. 26","I.D. 20/O.D. 26","I.D. 20/O.D. 26","I.D. 20/O.D. 26"]
["Decoration panel","Model","","","","BYK32GJW1","BYK32GJW1","BYK32GJW1","BYK63GJW1","BYK63GJW1","BYK63GJW1"]
["","Colour","","","","Fresh White","Fresh White","Fresh White","Fresh White","Fresh White","Fresh White"]
["","Dimensions","","Height","mm","80","80","80","80","80","80"]
["","","","Width","mm","950","950","950","1350","1350","1350"]
["","","","Depth","mm","550","550","550","550","550","550"]
["","Weight","","","kg","8","8","8","10","10","10"]
["Air filter","Type","","","","Removable / washable","Removable / washable","Removable / washable","Removable / washable","Removable / washable","Removable / washable"]
["Power supply","Name","","","","VE","VE","VE","VE","VE","VE"]
["","Phase","","","","1~","1~","1~","1~","1~","1~"]
["","Power supply-=-Frequency","","Frequency","","50/60","50/60","50/60","50/60","50/60","50/60"]
["","Power supply-=-Voltage","","Voltage","","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220"]
["Current - 50Hz","Current - 50Hz-=-Maximum fuse amps (MFA)","","Maximum fuse amps (MFA)","","6","6","6","6","6","6"]
["Required ceiling void >","mm","","","","260","260","260","260","260","260"]
["Standard Accessories","General safety precautions","","","","1","1","1","1","1","1"]
["","Sealing material (drain hose)","","","","1","1","1","1","1","1"]
["","Clamp for drain hose","","","","1","1","1","1","1","1"]
["","Drain hose","","","","1","1","1","1","1","1"]
["","Installation and operation manual","","","","1","1","1","1","1","1"]
["","Paper pattern for installation","","","","1","1","1","1","1","1"]
["Notes","","","","","(1) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m.","(1) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m.","(1) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m.","(1) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m.","(1) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m.","(1) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m."]
["","","","","","(2) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m.","(2) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m.","(2) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m.","(2) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m.","(2) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m.","(2) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m."]
["","","","","","(3) - The sound power level is an absolute value indicating the power which a sound source generates.","(3) - The sound power level is an absolute value indicating the power which a sound source generates.","(3) - The sound power level is an absolute value indicating the power which a sound source generates.","(3) - The sound power level is an absolute value indicating the power which a sound source generates.","(3) - The sound power level is an absolute value indicating the power which a sound source generates.","(3) - The sound power level is an absolute value indicating the power which a sound source generates."]
["","","","","","(4) - Instead of a fuse, use a circuit breaker","(4) - Instead of a fuse, use a circuit breaker","(4) - Instead of a fuse, use a circuit breaker","(4) - Instead of a fuse, use a circuit breaker","(4) - Instead of a fuse, use a circuit breaker","(4) - Instead of a fuse, use a circuit breaker"]
["","","","","","(5) - Select wire size based on the value of MCA","(5) - Select wire size based on the value of MCA","(5) - Select wire size based on the value of MCA","(5) - Select wire size based on the value of MCA","(5) - Select wire size based on the value of MCA","(5) - Select wire size based on the value of MCA"]