{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":55,"n_cols":7,"rows_kept":55,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FXMQ-MA"]
[]
[]
[]
[]
["","","","","","FXMQ200MAVE","FXMQ250MAVE"]
["Sound pressure level","Cooling","","At low fan speed","dBA","45","45"]
["","","","At high fan speed","dBA","48","48"]
["Standard Accessories","Installation and operation manual","","","","Installation and operation manual","Installation and operation manual"]
["","Connection pipes","","","","Connection pipes","Connection pipes"]
["","Sealing pads","","","","Sealing pads","Sealing pads"]
["","Clamps","","","","Clamps","Clamps"]
["","Screws","","","","Screws","Screws"]
["Refrigerant","Type","","","","R-410A","R-410A"]
["Power input - 50Hz","Cooling","","At high fan speed","kW","1.294","1.465"]
["","Heating","","At high fan speed","kW","1.294","1.465"]
["Cooling capacity","Total capacity","","At high fan speed","kW","22.4 (1)","28.0 (1)"]
["Piping connections","Liquid","","OD","mm","9.52","9.52"]
["","","","Type","","Flare connection","Flare connection"]
["","Gas","","OD","mm","19.1","22.2"]
["","","","Type","","Braze connection","Braze connection"]
["","Drain","","","","PS1B","PS1B"]
["Dimensions","Unit","","Width","mm","1,380","1,380"]
["","","","Depth","mm","1,100","1,100"]
["","","","Height","mm","470","470"]
["Casing","Material","","","","Galvanised steel plate","Galvanised steel plate"]
["Weight","Unit","","","kg","137","137"]
["Fan","External static pressure - 50Hz","","High","Pa","221 (4)","270 (4)"]
["","External static pressure - 60Hz","","High","Pa","270","270"]
["","Air flow rate - 50Hz","Cooling","At high fan speed","m³/min","58","72"]
["","","","At low fan speed","m³/min","50","62"]
["","Air flow rate - 60Hz","Cooling","High","m³/min","58","72"]
["","","","Low","m³/min","50","62"]
["Heating capacity","Total capacity","","At high fan speed","kW","25.0 (2)","31.5 (2)"]
["Current - 50Hz","Maximum fuse amps (MFA)","","","A","15","15"]
["Power supply","Phase","","","","1~","1~"]
["","Name","","","","VE","VE"]
["","Frequency","","","Hz","50/60","50/60"]
["","Voltage","","","V","220-240/220","220-240/220"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)"]
["","","","","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)"]
["","","","","","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat."]
["","","","","","(4) - The external static pressure is changeable: change the connectors inside the electrical box, this pressure means: High static pressure - Standard","(4) - The external static pressure is changeable: change the connectors inside the electrical box, this pressure means: High static pressure - Standard"]
["","","","","","(5) - Air filter is not standard accessory, but please mount it in the duct system of the suction side. Select its dust collection efficiency (gravity method) 50% and more.","(5) - Air filter is not standard accessory, but please mount it in the duct system of the suction side. Select its dust collection efficiency (gravity method) 50% and more."]
["","","","","","(6) - Sound pressure levels are measured at 220V.","(6) - Sound pressure levels are measured at 220V."]
["","","","","","(7) - Reference acoustic pressure 0 dB = 20 Pa.","(7) - Reference acoustic pressure 0 dB = 20 Pa."]
["","","","","","(8) - Sound values are measured in an anechoic room.","(8) - Sound values are measured in an anechoic room."]
["","","","","","(9) - Operation sound differs with operation and ambient conditions","(9) - Operation sound differs with operation and ambient conditions"]
["","","","","","(10) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(10) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(11) - Maximum allowable voltage range variation between phases is 2%.","(11) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(12) - MCA/MFA: MCA = 1.25 x FLA","(12) - MCA/MFA: MCA = 1.25 x FLA"]
["","","","","","(13) - MFA ≤ 4 x FLA","(13) - MFA ≤ 4 x FLA"]
["","","","","","(14) - Next lower standard fuse rating minimum 15A","(14) - Next lower standard fuse rating minimum 15A"]
["","","","","","(15) - Select wire size based on the value of MCA","(15) - Select wire size based on the value of MCA"]
["","","","","","(16) - Instead of a fuse, use a circuit breaker","(16) - Instead of a fuse, use a circuit breaker"]