{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":53,"n_cols":19,"rows_kept":53,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FXMQ-P7"]
[]
[]
[]
[]
["","","","","","FXMQ20P7VEB","FXMQ25P7VEB","FXMQ32P7VEB","FXMQ40P7VEB","FXMQ50P7VEB9","FXMQ50P7VEB","FXMQ63P7VEB9","FXMQ63P7VEB","FXMQ80P7VEB9","FXMQ80P7VEB","FXMQ100P7VEB9","FXMQ100P7VEB","FXMQ125P7VEB9","FXMQ125P7VEB"]
["Power input - 50Hz","Cooling","","At high fan speed","kW","0.049 (1)","0.049 (1)","0.053 (1)","0.151 (1)","0.110 (1)","0.110 (1)","0.120 (1)","0.120 (1)","0.171 (1)","0.171 (1)","0.176 (1)","0.176 (1)","0.241 (1)","0.241 (1)"]
["","Heating","","At high fan speed","kW","0.037 (2)","0.037 (2)","0.041 (2)","0.139 (2)","0.098 (2)","0.098 (2)","0.108 (2)","0.108 (2)","0.159 (2)","0.159 (2)","0.164 (2)","0.164 (2)","0.229 (2)","0.229 (2)"]
["Dimensions","Unit","","Height","mm","300","300","300","300","300","300","300","300","300","300","300","300","300","300"]
["","","","Width","mm","550","550","550","700","1000","1000","1000","1000","1000","1000","1400","1400","1400","1400"]
["","","","Depth","mm","700","700","700","700","700","700","700","700","700","700","700","700","700","700"]
["Weight","Unit","","","kg","23","23","23","26","35","35","35","35","35","35","46","46","46","46"]
["Casing","Colour","","","","Unpainted","Unpainted","Unpainted","Unpainted","Unpainted","Unpainted","Unpainted","Unpainted","Unpainted","Unpainted","Unpainted","Unpainted","Unpainted","Unpainted"]
["","Material","","","","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate"]
["Required ceiling void >","mm","","","","350","350","350","350","350","350","350","350","350","350","350","350","350","350"]
["Fan","Air flow rate - 50Hz","Cooling","At high fan speed","m³/min","9.0","9.0","9.5","16.0","18.0","18.0","19.5","19.5","25.0","25.0","32.0","32.0","39.0","39.0"]
["","","","At low fan speed","m³/min","6.5","6.5","7.0","11.0","15.0","15.0","16.0","16.0","20.0","20.0","23.0","23.0","28.0","28.0"]
["","External static pressure - 50Hz","","High","Pa","100","100","100","160","200","200","200","200","200","200","200","200","200","200"]
["","External static pressure - 60Hz","","High","Pa","100","100","100","160","200","200","200","200","200","200","200","200","200","200"]
["Refrigerant","Type","","","","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A"]
["Sound power level","Cooling","","At high fan speed","dBA","56","56","57","65","61.0","61","64.0","64","67.0","67","65.0","65","70.0","70"]
["Sound pressure level","Cooling","","At high fan speed","dBA","33","33","34","39","41.0","41","42.0","42","43.0","43","43.0","43","44.0","44"]
["","","","At medium fan speed","dBA","31","31","32.0","37","39.0","39","40.0","40","41.0","41","41.0","41","42.0","42"]
["","","","At low fan speed","dBA","29","29","30","35","37.0","37","38.0","38","39.0","39","39.0","39","40.0","40"]
["","Heating","","At high fan speed","dBA","33","33","34","39","41.0","41","42.0","42","43.0","43","43.0","43","44.0","44"]
["","","","At medium fan speed","dBA","31","31","32","37","39.0","39","40.0","40","41.0","41","41.0","41","42.0","42"]
["","","","At low fan speed","dBA","29","29","30","35","37.0","37","38.0","38","39.0","39","39.0","39","40.0","40"]
["Piping connections","Liquid","","Type","","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection"]
["","","","OD","mm","6.35","6.35","6.35","6.35","6.35","6.35","9.52","9.52","9.52","9.52","9.52","9.52","9.52","9.52"]
["","Gas","","Type","","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection"]
["","","","OD","mm","12.7","12.7","12.7","12.7","12.7","12.7","15.9","15.9","15.9","15.9","15.9","15.9","15.9","15.9"]
["","Drain","","","","VP25 (I.D. 25/O.D. 32)","VP25 (I.D. 25/O.D. 32)","VP25 (I.D. 25/O.D. 32)","VP25 (I.D. 25/O.D. 32)","VP25 (I.D. 25/O.D. 32)","VP25 (I.D. 25/O.D. 32)","VP25 (I.D. 25/O.D. 32)","VP25 (I.D. 25/O.D. 32)","VP25 (I.D. 25/O.D. 32)","VP25 (I.D. 25/O.D. 32)","VP25 (I.D. 25/O.D. 32)","VP25 (I.D. 25/O.D. 32)","VP25 (I.D. 25/O.D. 32)","VP25 (I.D. 25/O.D. 32)"]
["Decoration panel","Model","","","","BYBS32DJW1","BYBS32DJW1","BYBS32DJW1","BYBS45DJW1","BYBS71DJW1","BYBS71DJW1","BYBS71DJW1","BYBS71DJW1","BYBS71DJW1","BYBS71DJW1","BYBS125DJW1","BYBS125DJW1","BYBS125DJW1","BYBS125DJW1"]
["","Colour","","","","White (10Y9/0.5)","White (10Y9/0.5)","White (10Y9/0.5)","White (10Y9/0.5)","White (10Y9/0.5)","White (10Y9/0.5)","White (10Y9/0.5)","White (10Y9/0.5)","White (10Y9/0.5)","White (10Y9/0.5)","White (10Y9/0.5)","White (10Y9/0.5)","White (10Y9/0.5)","White (10Y9/0.5)"]
["","Dimensions","","Height","mm","55","55","55","55","55","55","55","55","55","55","55","55","55","55"]
["","","","Width","mm","650","650","650","800","1100","1100","1100","1100","1100","1100","1500","1500","1500","1500"]
["","","","Depth","mm","500","500","500","500","500","500","500","500","500","500","500","500","500","500"]
["","Weight","","","kg","3.0","3.0","3.0","3.5","4.5","4.5","4.5","4.5","4.5","4.5","6.5","6.5","6.5","6.5"]
["Drain-up height","mm","","","","625","625","625","625","625","625","625","625","625","625","625","625","625","625"]
["Air filter","Type","","","","Resin net","Resin net","Resin net","Resin net","Resin net","Resin net","Resin net","Resin net","Resin net","Resin net","Resin net","Resin net","Resin net","Resin net"]
["Power supply","Name","","","","VE","VE","VE","VE","VE","VE","VE","VE","VE","VE","VE","VE","VE","VE"]
["","Phase","","","","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~"]
["","Frequency","","","Hz","50/60","50/60","50/60","50/60","50/60","50/60","50/60","50/60","50/60","50/60","50/60","50/60","50/60","50/60"]
["","Voltage","","","V","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220 +/-10%","220-240/220","220-240/220 +/-10%","220-240/220","220-240/220 +/-10%","220-240/220","220-240/220 +/-10%","220-240/220","220-240/220 +/-10%","220-240/220"]
["Current - 50Hz","Maximum fuse amps (MFA)","","","A","16","16","16","16","16","16","16","16","16","16","16","16","16","16"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m"]
["","","","","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m"]
["","","","","","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat."]
["","","","","","(4) - The sound pressure values are mentioned for a unit installed with rear suction.","(4) - The sound pressure values are mentioned for a unit installed with rear suction.","(4) - The sound pressure values are mentioned for a unit installed with rear suction.","(4) - The sound pressure values are mentioned for a unit installed with rear suction.","","(4) - The sound pressure values are mentioned for a unit installed with rear suction.","","(4) - The sound pressure values are mentioned for a unit installed with rear suction.","","(4) - The sound pressure values are mentioned for a unit installed with rear suction.","","(4) - The sound pressure values are mentioned for a unit installed with rear suction.","","(4) - The sound pressure values are mentioned for a unit installed with rear suction."]
["","","","","","(5) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(5) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(5) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(5) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","","(5) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","","(5) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","","(5) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","","(5) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","","(5) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(6) - Maximum allowable voltage range variation between phases is 2%.","(6) - Maximum allowable voltage range variation between phases is 2%.","(6) - Maximum allowable voltage range variation between phases is 2%.","(6) - Maximum allowable voltage range variation between phases is 2%.","","(6) - Maximum allowable voltage range variation between phases is 2%.","","(6) - Maximum allowable voltage range variation between phases is 2%.","","(6) - Maximum allowable voltage range variation between phases is 2%.","","(6) - Maximum allowable voltage range variation between phases is 2%.","","(6) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(7) - Select wire size based on the value of MCA","(7) - Select wire size based on the value of MCA","(7) - Select wire size based on the value of MCA","(7) - Select wire size based on the value of MCA","","(7) - Select wire size based on the value of MCA","","(7) - Select wire size based on the value of MCA","","(7) - Select wire size based on the value of MCA","","(7) - Select wire size based on the value of MCA","","(7) - Select wire size based on the value of MCA"]
["","","","","","(8) - Use a circuit breaker instead of a fuse.","(8) - Use a circuit breaker instead of a fuse.","(8) - Use a circuit breaker instead of a fuse.","(8) - Use a circuit breaker instead of a fuse.","","(8) - Use a circuit breaker instead of a fuse.","","(8) - Use a circuit breaker instead of a fuse.","","(8) - Use a circuit breaker instead of a fuse.","","(8) - Use a circuit breaker instead of a fuse.","","(8) - Use a circuit breaker instead of a fuse."]