{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":55,"n_cols":6,"rows_kept":55,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FXMQ-PAVE"]
[]
[]
[]
[]
["","","","","","FXMQ140PAVE"]
["Sound pressure level","Cooling","","At low fan speed","dBA","43.0"]
["","","","Super high","dBA","46.0"]
["Standard Accessories","Operation manual","","","","Operation manual"]
["","Installation manual","","","","Installation manual"]
["","Drain hose","","","","Drain hose"]
["","Sealing pads","","","","Sealing pads"]
["","Clamps","","","","Clamps"]
["","Washer","","","","Washer"]
["","Screws","","","","Screws"]
["","Insulation for fitting","","","","Insulation for fitting"]
["","Clamp metal","","","","Clamp metal"]
["","Air discharge flange","","","","Air discharge flange"]
["","Air suction flange","","","","Air suction flange"]
["System","Connectable outdoor unit system","","","","R410A VRV Series"]
["Power input - 50Hz","Cooling","","At high fan speed","kW","0.461"]
["","Heating","","At high fan speed","kW","0.449"]
["Cooling capacity","Total capacity","","At high fan speed","kW","16.0 (1)"]
["Piping connections","Liquid","","OD","mm","9.5"]
["","","","Type","","Flare connection"]
["","Gas","","OD","mm","15.9"]
["","","","Type","","Flare connection"]
["","Drain","","","","VP25 (O.D. 32 / I.D. 25)"]
["Sound power level","Cooling","","At high fan speed","dBA","45.0"]
["Dimensions","Unit","","Width","mm","1,400"]
["","","","Depth","mm","700"]
["","","","Height","mm","300"]
["Casing","Material","","","","Galvanised steel plate"]
["Weight","Unit","","","kg","46"]
["Fan","External static pressure - 50Hz","","High","Pa","140"]
["","","","Low","Pa","50"]
["","External static pressure - 60Hz","","High","Pa","140"]
["","","","Low","Pa","50"]
["","Air flow rate - 50Hz","Cooling","At high fan speed","m³/min","39"]
["","","","At low fan speed","m³/min","32"]
["","","","Super high","m³/min","46"]
["","Air flow rate - 60Hz","Cooling","High","m³/min","39"]
["","","","Super high","m³/min","46"]
["","","","Low","m³/min","32"]
["Heating capacity","Total capacity","","At high fan speed","kW","18.0 (2)"]
["Current - 50Hz","Maximum fuse amps (MFA)","","","A","16"]
["Power supply","Phase","","","","1~"]
["","Name","","","","VE"]
["","Frequency","","","Hz","50/60"]
["","Voltage","","","V","220-240/220"]
["Notes","","","","","(1) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m."]
["","","","","","(2) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m."]
["","","","","","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat."]
["","","","","","(4) - External static pressure is changeable in 7 stages (20, 25, 32 class); 13 stages (40 class); 14 stages (50, 63, 80, 100, 125 class); 10 stages (140 class) within the range of the remote control."]
["","","","","","(5) - Air filter is not standard accessory, but please mount it in the duct system of the suction side. Select its dust collection efficiency (gravity method) 50% and more."]