{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":77,"n_cols":14,"rows_kept":77,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","LREQ-BY1"]
[]
[]
[]
[]
["","","","","","LREQ5B7Y1","LREQ6B7Y1","LREQ8B7Y1","LREQ10B7Y1","LREQ12B7Y1","LREQ15B7Y1","LREQ20B7Y1","LREQ30B7Y1","LREQ40B7Y1"]
["Refrigerating capacity","Low temperature","","Nom.","kW","5.51 (2)","6.51 (2)","8.33 (2)","10.0 (2)","10.7 (2)","13.9 (2)","15.4 (2)","27.8","29.6"]
["","Medium temperature","","Nom.","kW","12.5 (1)","15.2 (1)","19.8 (1)","23.8 (1)","26.5 (1)","33.9 (1)","37.9 (1)","67.8 (3)","75.8 (3)"]
["Power input","Low temperature","","Nom.","kW","4.65 (2)","5.88 (2)","7.72 (2)","9.27 (2)","9.89 (2)","12.8 (2)","14.1 (2)","25.6","27.6"]
["","Medium temperature","","Nom.","kW","5.1","6.56 (1)","8.76 (1)","10.6 (1)","12.0 (1)","15.2 (1)","17.0 (1)","30.4","34.0"]
["Operation range","Ambient temperature","","Min.","°C","-20","-20","-20","-20","-20","-20","-20"]
["","","","Max.","°C","43","43","43","43","43","43","43"]
["","Evaporator","Cooling","Min.","°CDB","-45","-45","-45","-45","-45","-45","-45"]
["","","","Max.","°CDB","10","10","10","10","10","10","10"]
["Annual electricity consumption Q","R-410A","","Te -10°C","kWh/a","19907","24681","33483","42794","46377","61683","72030"]
["","","","Te -35°C","kWh/a","22805","27453","33817","39747","44363","61090","67325"]
["Seasonal energy performance ratio SEPR","R-410A","","Te -10°C","","3.86","3.79","3.64","3.42","3.51","3.38","3.23"]
["","","","Te -35°C","","1.80","1.77","1.84","1.88","1.80","1.70","1.70"]
["Parameters at full load and ambient temp. 32°C (Point A)","R-410A","Te -10°C","Rated  cooling capacity (PA)","kW","12.50","15.20","19.80","23.80","26.50","33.90","37.90"]
["","","","Rated  power input (DA)","kW","5.10","6.56","8.76","10.60","12.00","15.20","17.00"]
["","","","Rated COP (COPA)","","2.45","2.32","2.26","2.25","2.21","2.23","2.23"]
["","","Te -35°C","Rated  cooling capacity (PA)","kW","5.51","6.51","8.33","10.00","10.70","13.90","15.40"]
["","","","Rated  power input (DA)","kW","4.65","5.88","7.72","9.27","9.89","12.80","14.10"]
["","","","Rated COP (COPA)","","1.18","1.11","1.08","1.08","1.08","1.09","1.09"]
["Parameters at full load and ambient temp. 43°C","R-410A","Te -10°C","Declared COP (COP3)","","1.54","1.57","1.40","1.46","1.47","1.46","1.51"]
["","","Te -35°C","Declared COP (COP3)","","0.76","0.74","0.68","0.70","0.71","0.71","0.74"]
["Compressor 2","Type","","","","","","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor"]
["Fan motor","Drive","","","","Direct drive","Direct drive","Direct drive","Direct drive","Direct drive","Direct drive","Direct drive"]
["Fan motor 2","Output","","","W","","","","","","350","750"]
["Fan","Quantity","","","","1","1","1","1","1","2","2"]
["","Type","","","","Propeller fan","Propeller fan","Propeller fan","Propeller fan","Propeller fan","Propeller fan","Propeller fan"]
["","Air flow rate","Cooling","Nom.","m³/min","95","102","171","179","191","230","240"]
["Fan motor","Output","","","W","350","350","750","750","750","350","750"]
["Piping connections","Liquid","","50m or less","","ø 9.5 C1220T (Brazing connection)","ø 9.5 C1220T (Brazing connection)","ø 9.5 C1220T (Brazing connection)","ø 9.5 C1220T (Brazing connection)","ø 12.7 C1220T (Brazing connection)","ø 12.7 C1220T (Brazing connection)","ø 12.7 C1220T (Brazing connection)","ø 19.05 C1220T (Brazing connection)","ø 19.05 C1220T (Brazing connection)"]
["","","","50~130m","","Ø 9.5 C1220T (Brazing connection)","Ø 9.5 C1220T (Brazing connection)","Ø 12.7 C1220T (Brazing connection)","Ø 12.7 C1220T (Brazing connection)","Ø 12.7 C1220T (Brazing connection)","Ø 12.7 C1220T (Brazing connection)","Ø 12.7 C1220T (Brazing connection)","ø 19.05 C1220T (Brazing connection)","ø 19.05 C1220T (Brazing connection)"]
["","Gas","","50m or less","","ø 22.2 C1220T (Brazing connection)","ø 22.2 C1220T (Brazing connection)","ø 28.6 C1220T (Brazing connection)","ø 28.6 C1220T (Brazing connection)","ø 28.6 C1220T (Brazing connection)","ø 34.9 C1220T (Brazing connection)","ø 34.9 C1220T (Brazing connection)","ø 41.28 C1220T (Brazing connection)","ø 41.28 C1220T (Brazing connection)"]
["","","","50~130m","","ø 22.2 C1220T (Brazing connection)","ø 22.2 C1220T (Brazing connection)","Ø 28.6 C1220T (Brazing connection)","Ø 28.6 C1220T (Brazing connection)","Ø 28.6 C1220T (Brazing connection)","ø 34.9 C1220T (Brazing connection)","ø 34.9 C1220T (Brazing connection)","ø 41.28 C1220T (Brazing connection)","ø 41.28 C1220T (Brazing connection)"]
["Dimensions","Unit","","Height","mm","1680","1680","1680","1680","1680","1680","1680"]
["","","","Width","mm","635","635","930","930","930","1240","1240"]
["","","","Depth","mm","765","765","765","765","765","765","765"]
["Weight","Unit","","","kg","166","166","242","242","242","331","337"]
["Refrigerant","Type","","","","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A"]
["Casing","Colour","","","","Ivory white (Munsell code: 5Y7.5/1)","Ivory white (Munsell code: 5Y7.5/1)","Ivory white (Munsell code: 5Y7.5/1)","Ivory white (Munsell code: 5Y7.5/1)","Ivory white (Munsell code: 5Y7.5/1)","Ivory white (Munsell code: 5Y7.5/1)","Ivory white (Munsell code: 5Y7.5/1)"]
["Refrigerant","GWP","","","","2087.5","2087.5","2087.5","2087.5","2087.5","2087.5","2087.5"]
["Heat exchanger","Type","","","","Cross fin coil","Cross fin coil","Cross fin coil","Cross fin coil","Cross fin coil","Cross fin coil","Cross fin coil"]
["Refrigerant","Charge","","","kg","5.2","5.2","7.9","7.9","7.9","11.5","11.5"]
["","Charge","","","tCO2Eq","10.9","10.9","16.5","16.5","16.5","24.0","24.0"]
["Standard Accessories","Installation manual","","","","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual"]
["","Clamping materials","","","","Clamping materials","Clamping materials","Clamping materials","Clamping materials","Clamping materials","Clamping materials","Clamping materials","Clamping materials","Clamping materials"]
["","Refrigerant label for F-gas regulation","","","","Refrigerant label for F-gas regulation","Refrigerant label for F-gas regulation","Refrigerant label for F-gas regulation","Refrigerant label for F-gas regulation","Refrigerant label for F-gas regulation","Refrigerant label for F-gas regulation","Refrigerant label for F-gas regulation","Refrigerant label for F-gas regulation","Refrigerant label for F-gas regulation"]
["","Operation manual","","","","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual"]
["","Connection pipes","","","","Connection pipes","Connection pipes","Connection pipes","Connection pipes","Connection pipes","Connection pipes","Connection pipes","Connection pipes","Connection pipes"]
["","Additional refrigerant label","","","","Additional refrigerant label","Additional refrigerant label","Additional refrigerant label","Additional refrigerant label","Additional refrigerant label","Additional refrigerant label","Additional refrigerant label"]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~","3~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50"]
["","Voltage","","","V","380-415","380-415","380-415","380-415","380-415","380-415","380-415"]
["Current","Nominal running current (RLA) - 50Hz","Compressor 2","Cooling","A","","","7.5","7.9","8.3","8.2","8.4"]
["","","Compressor 1","Cooling","A","7.1","9.2","5.3","7.4","9.8","7.0","9.5"]
["","","Compressor 3","Cooling","A","","","","","","8.2","8.4"]
["Notes","","","","","(1) - Cooling: evaporating temp. -10°C; outdoor temp. 32°C; suction SH10°C","(1) - Cooling: evaporating temp. -10°C; outdoor temp. 32°C; suction SH10°C","(1) - Cooling: evaporating temp. -10°C; outdoor temp. 32°C; suction SH10°C","(1) - Cooling: evaporating temp. -10°C; outdoor temp. 32°C; suction SH10°C","(1) - Cooling: evaporating temp. -10°C; outdoor temp. 32°C; suction SH10°C","(1) - Cooling: evaporating temp. -10°C; outdoor temp. 32°C; suction SH10°C","(1) - Cooling: evaporating temp. -10°C; outdoor temp. 32°C; suction SH10°C","(1) - When target evaporating temperature is -20°C or lower, there is the possibility to add the refrigerant oil. If the refrigerant oil is added, the target evaporating temperature can not change to -20°C or higher.","(1) - When target evaporating temperature is -20°C or lower, there is the possibility to add the refrigerant oil. If the refrigerant oil is added, the target evaporating temperature can not change to -20°C or higher."]
["","","","","","(2) - Cooling: evaporating temp. -35°C; outdoor temp. 32°C; suction SH10°C","(2) - Cooling: evaporating temp. -35°C; outdoor temp. 32°C; suction SH10°C","(2) - Cooling: evaporating temp. -35°C; outdoor temp. 32°C; suction SH10°C","(2) - Cooling: evaporating temp. -35°C; outdoor temp. 32°C; suction SH10°C","(2) - Cooling: evaporating temp. -35°C; outdoor temp. 32°C; suction SH10°C","(2) - Cooling: evaporating temp. -35°C; outdoor temp. 32°C; suction SH10°C","(2) - Cooling: evaporating temp. -35°C; outdoor temp. 32°C; suction SH10°C","(2) - In the usage environment which outdoor temperature becomes lower than -10°C, installation of windbreak board or snowbreak hood is needed. For details, see the service manual.","(2) - In the usage environment which outdoor temperature becomes lower than -10°C, installation of windbreak board or snowbreak hood is needed. For details, see the service manual."]
["","","","","","(3) - Sound pressure data: measured at 1m in front of unit, at 1.5m height","(3) - Sound pressure data: measured at 1m in front of unit, at 1.5m height","(3) - Sound pressure data: measured at 1m in front of unit, at 1.5m height","(3) - Sound pressure data: measured at 1m in front of unit, at 1.5m height","(3) - Sound pressure data: measured at 1m in front of unit, at 1.5m height","(3) - Sound pressure data: measured at 1m in front of unit, at 1.5m height","(3) - Sound pressure data: measured at 1m in front of unit, at 1.5m height","(3) - Operation conditions of outside unit: evaporating temperature = -10°C, outdoor temperature +32°C, Suction SH 10K","(3) - Operation conditions of outside unit: evaporating temperature = -10°C, outdoor temperature +32°C, Suction SH 10K"]
["","","","","","(4) - RLA is based on following conditions: outdoor temp. 32°CDB; suction SH 10°C; saturated temperature equivalent to suction pressure -10°C","(4) - RLA is based on following conditions: outdoor temp. 32°CDB; suction SH 10°C; saturated temperature equivalent to suction pressure -10°C","(4) - RLA is based on following conditions: outdoor temp. 32°CDB; suction SH 10°C; saturated temperature equivalent to suction pressure -10°C","(4) - RLA is based on following conditions: outdoor temp. 32°CDB; suction SH 10°C; saturated temperature equivalent to suction pressure -10°C","(4) - RLA is based on following conditions: outdoor temp. 32°CDB; suction SH 10°C; saturated temperature equivalent to suction pressure -10°C","(4) - RLA is based on following conditions: outdoor temp. 32°CDB; suction SH 10°C; saturated temperature equivalent to suction pressure -10°C","(4) - RLA is based on following conditions: outdoor temp. 32°CDB; suction SH 10°C; saturated temperature equivalent to suction pressure -10°C","(4) - Have to use the Branch Pipe Kit (EKHRQZM) to divide a suction pipe between the outdoor units.","(4) - Have to use the Branch Pipe Kit (EKHRQZM) to divide a suction pipe between the outdoor units."]
["","","","","","(5) - TOCA means the total value of each OC set.","(5) - TOCA means the total value of each OC set.","(5) - TOCA means the total value of each OC set.","(5) - TOCA means the total value of each OC set.","(5) - TOCA means the total value of each OC set.","(5) - TOCA means the total value of each OC set.","(5) - TOCA means the total value of each OC set.","(5) - Have to use the refrigerant oil of DAIKIN service parts. (1 liter can: parts no, 5004333)","(5) - Have to use the refrigerant oil of DAIKIN service parts. (1 liter can: parts no, 5004333)"]
["","","","","","(6) - MSC means the maximum current during start up of the compressor","(6) - MSC means the maximum current during start up of the compressor","(6) - MSC means the maximum current during start up of the compressor","(6) - MSC means the maximum current during start up of the compressor","(6) - MSC means the maximum current during start up of the compressor","(6) - MSC means the maximum current during start up of the compressor","(6) - MSC means the maximum current during start up of the compressor","(6) - RLA is based on the following conditions: outdoor temperature: 32°C; Suction SH. 10K; Evaporating temperature -10°C.","(6) - RLA is based on the following conditions: outdoor temperature: 32°C; Suction SH. 10K; Evaporating temperature -10°C."]
["","","","","","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - TOCA means the total value of each OC set.","(7) - TOCA means the total value of each OC set."]
["","","","","","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(8) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(9) - Select wire size based on the larger value of MCA or TOCA","(9) - Select wire size based on the larger value of MCA or TOCA","(9) - Select wire size based on the larger value of MCA or TOCA","(9) - Select wire size based on the larger value of MCA or TOCA","(9) - Select wire size based on the larger value of MCA or TOCA","(9) - Select wire size based on the larger value of MCA or TOCA","(9) - Select wire size based on the larger value of MCA or TOCA","(9) - Maximum allowable voltage range variation between phases is 2%.","(9) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","","(11) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN 61000-3-2","(11) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN 61000-3-2","(11) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN 61000-3-2","(11) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN 61000-3-2","(11) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN 61000-3-2","(11) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN 61000-3-2","(11) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN 61000-3-2","(11) - Compressor 2 and 3","(11) - Compressor 2 and 3"]
["","","","","","(12) - Compressor 1","(12) - Compressor 1","(12) - Compressor 1","(12) - Compressor 1","(12) - Compressor 1","(12) - Compressor 1","(12) - Compressor 1"]
["","","","","","(13) - Compressor 2","(13) - Compressor 2","(13) - Compressor 2","(13) - Compressor 2","(13) - Compressor 2","(13) - Compressor 2","(13) - Compressor 2"]
["","","","","","(14) - Compressor 2 and 3","(14) - Compressor 2 and 3","(14) - Compressor 2 and 3","(14) - Compressor 2 and 3","(14) - Compressor 2 and 3","(14) - Compressor 2 and 3","(14) - Compressor 2 and 3"]
["","","","","","(15) - Factory charge of unit","(15) - Factory charge of unit","(15) - Factory charge of unit","(15) - Factory charge of unit","(15) - Factory charge of unit","(15) - Factory charge of unit","(15) - Factory charge of unit"]
["","","","","","(16) - Contains fluorinated greenhouse gases","(16) - Contains fluorinated greenhouse gases","(16) - Contains fluorinated greenhouse gases","(16) - Contains fluorinated greenhouse gases","(16) - Contains fluorinated greenhouse gases","(16) - Contains fluorinated greenhouse gases","(16) - Contains fluorinated greenhouse gases"]
["","","","","","(17) - Ecodesign Regulation: (EU) 2015/1095","(17) - Ecodesign Regulation: (EU) 2015/1095","(17) - Ecodesign Regulation: (EU) 2015/1095","(17) - Ecodesign Regulation: (EU) 2015/1095","(17) - Ecodesign Regulation: (EU) 2015/1095","(17) - Ecodesign Regulation: (EU) 2015/1095","(17) - Ecodesign Regulation: (EU) 2015/1095"]
["Standard Accessories","Ref. oil fill volume label","","","","","","","","","","","Ref. oil fill volume label","Ref. oil fill volume label"]