{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":47,"n_cols":5,"rows_kept":47,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","REMQ-T"]
[]
[]
[]
[]
["","","","","REMQ5T7Y1B"]
["Cooling capacity","Prated,c","","kW","14"]
["Capacity range","HP","","","5"]
["Maximum number of connectable indoor units","","","","64 (3)"]
["Indoor index connection","Min.","","","62.5"]
["","Max.","","","162.5"]
["Dimensions","Unit","Height","mm","1685"]
["","","Width","mm","930"]
["","","Depth","mm","765"]
["Weight","Unit","","kg","210"]
["Fan","External static pressure","Max.","Pa","78"]
["Compressor","Type","","","Hermetically sealed scroll compressor"]
["Operation range","Cooling","Min.","°CDB","-5"]
["","","Max.","°CDB","43"]
["","Heating","Min.","°CWB","-20"]
["","","Max.","°CWB","15.5"]
["Sound power level","Cooling","Nom.","dBA","77.0 (4)"]
["Sound pressure level","Cooling","Nom.","dBA","56"]
["Refrigerant","Type","","","R-410A"]
["","GWP","","","2087.5"]
["","Charge","","tCO2Eq","20.2"]
["","Charge","","kg","9.7"]
["Piping connections","Liquid","OD","mm","9.52"]
["","Gas","OD","mm","19.1"]
["","HP/LP gas","OD","mm","15.9"]
["Standard Accessories","Connection pipes","","","1"]
["","Installation and operation manual","","","1"]
["Power supply","Name","","","Y1"]
["","Phase","","","3N~"]
["","Frequency","","Hz","50"]
["","Voltage","","V","380-415"]
["Notes","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m"]
["","","","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m"]
["","","","","(3) - Actual number of connectable indoor units depends on the indoor unit type and the connection ratio restriction for the system (50% ≤ CR ≤ 120%)"]
["","","","","(4) - Sound power level is an absolute value that a sound source generates."]
["","","","","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings."]
["","","","","(6) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB"]
["","","","","(7) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value"]
["","","","","(8) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current."]
["","","","","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","(10) - TOCA means the total value of each OC set."]
["","","","","(11) - FLA means the nominal running current of the fan"]