{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":87,"n_cols":27,"rows_kept":87,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RQYQ-P"]
[]
[]
[]
[]
["","","","","","RQYQ140PY1","RQYQ18PY1","RQYQ20PY1","RQYQ22PY1","RQYQ24PY1","RQYQ26PY1","RQYQ28PY1","RQYQ30PY1","RQYQ32PY1","RQYQ34PY1","RQYQ36PY1","RQYQ38PY1","RQYQ40PY1","RQYQ42PY1","RQYQ44PY1","RQYQ46PY1","RQYQ48PY1","RQYQ8PY1B","RQYQ10PY1B","RQYQ12PY1B","RQYQ14PY1B","RQYQ16PY1B"]
["Sound pressure level","Cooling","","Nom.","dBA","","61","62","63","63","63","63","63","63","64","64","65","65","65","65","65","65","57.0","58.0","60.0","60.0","60.0"]
["Standard Accessories","Installation manual","","","","Installation manual","","","","","","","","","","","","","","","","","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual"]
["","Operation manual","","","","Operation manual","","","","","","","","","","","","","","","","","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual"]
["","Clamps","","","","Clamps","","","","","","","","","","","","","","","","","Clamps","Clamps","Clamps","Clamps","Clamps"]
["Capacity range","HP","","","","5","18","20","22","24","26","28","30","32","34","36","38","40","42","44","46","48","8","10","12","14","16"]
["Operation range","Cooling","","Max.","°CDB","43","43","43","43","43","43","43","43","43","43","43","43","43","43","43","43","43","43","43","43","43","43"]
["","","","Min.","°CDB","-5","-5","-5","-5","-5","-5","-5","-5","-5","-5","-5","-5","-5","-5","-5","-5","-5","-5","-5","-5","-5","-5"]
["","Heating","","Min.","°CWB","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20"]
["","","","Max.","°CWB","15.5","15.5","15.5","15.5","15.5","15.5","15.5","15.5","15.5","15.5","15.5","15.5","15.5","15.5","15.5","15.5","15.5","15.5","15.5","15.5","15.5","15.5"]
["Maximum number of connectable indoor units","","","","","10","39","43","47","52","56","60","64","64","64","64","64","64","64","64","64","64","17","21","26","30","34"]
["Space cooling","B Condition (30°C - 27/19)","","Pdc","kW","10.3"]
["","","","EERd","","4.40"]
["","D Condition (20°C - 27/19)","","Pdc","kW","5.01"]
["","","","EERd","","9.29"]
["","A Condition (35°C - 27/19)","","EERd","","2.54"]
["","","","Pdc","kW","14.0"]
["","C Condition (25°C - 27/19)","","EERd","","7.31"]
["","","","Pdc","kW","6.63"]
["Compressor","Type","","","","Hermetically sealed scroll compressor","","","","","","","","","","","","","","","","","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor"]
["Weight","Unit","","","kg","175","","","","","","","","","","","","","","","","","230","284","284","381","381"]
["Refrigerant","Charge","","","TCO2Eq","23.2"]
["","GWP","","","","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5"]
["","Charge","","","kg","11.1","","","","","","","","","","","","","","","","","10.8","11.7","11.7","11.7","11.7"]
["","Type","","","","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A"]
["System","Outdoor unit module 2","","","","","RQYQ10P","RQYQ12P","RQYQ12P","RQYQ12P","RQYQ16P","RQYQ16P","RQYQ16P","RQYQ16P","RQYQ10P","RQYQ10P","RQYQ12P","RQYQ12P","RQYQ16P","RQYQ16P","RQYQ16P","RQYQ16P"]
["","Outdoor unit module 3","","","","","","","","","","","","","RQYQ14P","RQYQ16P","RQYQ16P","RQYQ16P","RQYQ16P","RQYQ16P","RQYQ16P","RQYQ16P"]
["","Outdoor unit module 1","","","","RQYQ140P","RQYQ8P","RQYQ8P","RQYQ10P","RQYQ12P","RQYQ10P","RQYQ12P","RQYQ14P","RQYQ16P","RQYQ10P","RQYQ10P","RQYQ10P","RQYQ12P","RQYQ10P","RQYQ12P","RQYQ14P","RQYQ16P","RQYQ8P","RQYQ10P","RQYQ12P","RQYQ14P","RQYQ16P"]
["Power input - 50Hz","Cooling","Nom.","35°CDB","kW","","","","","","","","","","","","","","","","","","5.24","7.64","10.10","11.6","13.6"]
["","Heating","Nom.","6°CWB","kW","","","","","","","","","","","","","","","","","","6.42","8.59","10.20","12.2","13.6"]
["Indoor index connection","Nom.","","","","125","450","500","550","600","650","700","750","800","850","900","950","1,000","1,050","1,100","1,150","1,200","200","250","300","350","400"]
["","Min.","","","","62.5","225","250","275","300","325","350","375","400","425","450","475","500","525","550","575","600","100","125","150","175","200"]
["","Max.","","","","162.5","585","650","715","780","845","910","975","1,040","1,105","1,170","1,235","1,300","1,365","1,430","1,495","1,560","260","325","390","455","520"]
["Cooling capacity","Prated,c","","","kW","14.0"]
["Recommended combination","","","","","4 x FXSQ32A2VEB"]
["Space heating (Average climate)","TOL","","COPd (declared COP)","","1.92"]
["","","","Pdh (declared heating cap)","kW","8.5"]
["","D Condition (12°C)","","Pdh (declared heating cap)","kW","4.18"]
["","","","COPd (declared COP)","","6.43"]
["","B Condition (2°C)","","COPd (declared COP)","","3.42"]
["","","","Pdh (declared heating cap)","kW","4.58"]
["","C Condition (7°C)","","COPd (declared COP)","","4.84"]
["","","","Pdh (declared heating cap)","kW","3.29"]
["","A Condition (-7°C)","","COPd (declared COP)","","2.20"]
["","","","Pdh (declared heating cap)","kW","7.52"]
["","TBivalent","","Pdh (declared heating cap)","kW","8.5"]
["","","","Tbiv (bivalent temperature)","°C","-10"]
["","","","COPd (declared COP)","","1.92"]
["Piping connections","Liquid","","OD","mm","9.52","15.9","15.9","15.9","15.9","19.1","19.1","19.1","19.1","19.1","19.1","19.1","19.1","19.1","19.1","19.1","19.1","9.52","9.52","12.70","12.70","12.70"]
["","","","Type","","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection"]
["","Total piping length","System","Actual","m","300","300","300","300","300","300","300","300","300","300","300","300","300","300","300","300","300","300","300","300","300","300"]
["","Gas","","OD","mm","15.9","28.6","28.6","28.6","34.9","34.9","34.9","34.9","34.9","34.9","41.3","41.3","41.3","41.3","41.3","41.3","41.3","19.1","22.2","28.6","28.6","28.6"]
["","","","Type","","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection"]
["","Level difference","OU - IU","Outdoor unit in highest position","m","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50"]
["","","","Indoor unit in highest position","m","40","40","40","40","40","40","40","40","40","40","40","40","40","40","40","40","40","40","40","40","40","40"]
["","","IU - IU","Max.","m","15","15","15","15","15","15","15","15","15","15","15","15","15","15","15","15","15","15","15","15","15","15"]
["Sound power level","Cooling","","Nom.","dBA","79"]
["Dimensions","Unit","","Width","mm","635","","","","","","","","","","","","","","","","","930","930","930","1,240","1,240"]
["","","","Depth","mm","765","","","","","","","","","","","","","","","","","765","765","765","765","765"]
["","","","Height","mm","1,680","","","","","","","","","","","","","","","","","1,680","1,680","1,680","1,680","1,680"]
["EER at nom. capacity","35°CDB","","","kW/kW","","","","","","","","","","","","","","","","","","4.27","3.66","3.32","3.45","3.31"]
["Fan","External static pressure","","Max.","Pa","78","78","78","78","78","78","78","78","78","78","78","78","78","78","78","78","78","78","78","78","78","78"]
["","Air flow rate","Cooling","Nom.","m³/min","","","","","","","","","","","","","","","","","","180","185","200","233","233"]
["Heating capacity","Prated,h","","","kW","16.0"]
["","Nom.","","6°CWB","kW","","","","","","","","","","","","","","","","","","25.0 (2)","31.5 (2)","37.5 (2)","45.0 (2)","50.0 (2)"]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Name","","","","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m"]
["","","","","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m"]
["","","","","","(3) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(3) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(3) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(3) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(3) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(3) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(3) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(3) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(3) - TOCA means the total value of each OC set.","(3) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(3) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(3) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(3) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(3) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(3) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(3) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(3) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(3) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(3) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(3) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(3) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(3) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB"]
["","","","","","(4) - TOCA means the total value of each OC set.","(4) - TOCA means the total value of each OC set.","(4) - TOCA means the total value of each OC set.","(4) - TOCA means the total value of each OC set.","(4) - TOCA means the total value of each OC set.","(4) - TOCA means the total value of each OC set.","(4) - TOCA means the total value of each OC set.","(4) - TOCA means the total value of each OC set.","(4) - MSC means the maximum current during start up of the compressor","(4) - TOCA means the total value of each OC set.","(4) - TOCA means the total value of each OC set.","(4) - TOCA means the total value of each OC set.","(4) - TOCA means the total value of each OC set.","(4) - TOCA means the total value of each OC set.","(4) - TOCA means the total value of each OC set.","(4) - TOCA means the total value of each OC set.","(4) - TOCA means the total value of each OC set.","(4) - TOCA means the total value of each OC set.","(4) - TOCA means the total value of each OC set.","(4) - TOCA means the total value of each OC set.","(4) - TOCA means the total value of each OC set.","(4) - TOCA means the total value of each OC set."]
["","","","","","(5) - MSC means the maximum current during start up of the compressor","(5) - MSC means the maximum current during start up of the compressor","(5) - MSC means the maximum current during start up of the compressor","(5) - MSC means the maximum current during start up of the compressor","(5) - MSC means the maximum current during start up of the compressor","(5) - MSC means the maximum current during start up of the compressor","(5) - MSC means the maximum current during start up of the compressor","(5) - MSC means the maximum current during start up of the compressor","(5) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(5) - MSC means the maximum current during start up of the compressor","(5) - MSC means the maximum current during start up of the compressor","(5) - MSC means the maximum current during start up of the compressor","(5) - MSC means the maximum current during start up of the compressor","(5) - MSC means the maximum current during start up of the compressor","(5) - MSC means the maximum current during start up of the compressor","(5) - MSC means the maximum current during start up of the compressor","(5) - MSC means the maximum current during start up of the compressor","(5) - MSC means the maximum current during start up of the compressor","(5) - MSC means the maximum current during start up of the compressor","(5) - MSC means the maximum current during start up of the compressor","(5) - MSC means the maximum current during start up of the compressor","(5) - MSC means the maximum current during start up of the compressor"]
["","","","","","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Maximum allowable voltage range variation between phases is 2%.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Select wire size based on the value of MCA or TOCA.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(8) - Select wire size based on the larger value of MCA or TOCA","(8) - Select wire size based on the value of MCA","(8) - Select wire size based on the value of MCA","(8) - Select wire size based on the value of MCA","(8) - Select wire size based on the value of MCA","(8) - Select wire size based on the value of MCA","(8) - Select wire size based on the value of MCA","(8) - Select wire size based on the value of MCA","(8) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(8) - Select wire size based on the value of MCA","(8) - Select wire size based on the value of MCA","(8) - Select wire size based on the value of MCA","(8) - Select wire size based on the value of MCA","(8) - Select wire size based on the value of MCA","(8) - Select wire size based on the value of MCA","(8) - Select wire size based on the value of MCA","(8) - Select wire size based on the value of MCA","(8) - Select wire size based on the value of MCA","(8) - Select wire size based on the value of MCA","(8) - Select wire size based on the value of MCA","(8) - Select wire size based on the value of MCA","(8) - Select wire size based on the value of MCA"]
["","","","","","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(9) - Sound values are measured in an anechoic chamber. Operating sound level generally becomes higher than this value depending on the operating conditions, reflected sound, and peripheral noise.","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","","(10) - Sound values are measured in an anechoic chamber. Operating sound level generally becomes higher than this value depending on the operating conditions, reflected sound, and peripheral noise.","(10) - Sound values are measured in an anechoic chamber. Operating sound level generally becomes higher than this value depending on the operating conditions, reflected sound, and peripheral noise.","(10) - Sound values are measured in an anechoic chamber. Operating sound level generally becomes higher than this value depending on the operating conditions, reflected sound, and peripheral noise.","(10) - Sound values are measured in an anechoic chamber. Operating sound level generally becomes higher than this value depending on the operating conditions, reflected sound, and peripheral noise.","(10) - Sound values are measured in an anechoic chamber. Operating sound level generally becomes higher than this value depending on the operating conditions, reflected sound, and peripheral noise.","(10) - Sound values are measured in an anechoic chamber. Operating sound level generally becomes higher than this value depending on the operating conditions, reflected sound, and peripheral noise.","(10) - Sound values are measured in an anechoic chamber. Operating sound level generally becomes higher than this value depending on the operating conditions, reflected sound, and peripheral noise.","(10) - Sound values are measured in an anechoic chamber. Operating sound level generally becomes higher than this value depending on the operating conditions, reflected sound, and peripheral noise.","(10) - Contains fluorinated greenhouse gases","(10) - Contains fluorinated greenhouse gases","(10) - Contains fluorinated greenhouse gases","(10) - Contains fluorinated greenhouse gases","(10) - Contains fluorinated greenhouse gases","(10) - Contains fluorinated greenhouse gases","(10) - Contains fluorinated greenhouse gases","(10) - Contains fluorinated greenhouse gases","(10) - Contains fluorinated greenhouse gases","(10) - Sound values are measured in an anechoic chamber. Operating sound level generally becomes higher than this value depending on the operating conditions, reflected sound, and peripheral noise.","(10) - Sound values are measured in an anechoic chamber. Operating sound level generally becomes higher than this value depending on the operating conditions, reflected sound, and peripheral noise.","(10) - Sound values are measured in an anechoic chamber. Operating sound level generally becomes higher than this value depending on the operating conditions, reflected sound, and peripheral noise.","(10) - Sound values are measured in an anechoic chamber. Operating sound level generally becomes higher than this value depending on the operating conditions, reflected sound, and peripheral noise.","(10) - Sound values are measured in an anechoic chamber. Operating sound level generally becomes higher than this value depending on the operating conditions, reflected sound, and peripheral noise."]
["","","","","","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","","","","","","","","","","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases"]
["Cooling capacity","Nom.","","35°CDB","kW","","","","","","","","","","","","","","","","","","22.4 (1)","28.0 (1)","33.5 (1)","40.0 (1)","45.0 (1)"]
["Standard Accessories","Connection pipes","","","","","","","","","","","","","","","","","","","","","Connection pipes","Connection pipes","Connection pipes","Connection pipes","Connection pipes"]