{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":81,"n_cols":14,"rows_kept":81,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RWEYQ-T"]
[]
[]
[]
[]
["","","","","","RWEYQ8T7Y1B (Archived)","RWEYQ10T7Y1B (Archived)","RWEYQ16T7Y1B (Archived)","RWEYQ18T7Y1B (Archived)","RWEYQ20T7Y1B (Archived)","RWEYQ24T7Y1B (Archived)","RWEYQ26T7Y1B (Archived)","RWEYQ28T7Y1B (Archived)","RWEYQ30T7Y1B (Archived)"]
["Sound pressure level","Cooling","","Nom.","dBA","50","51","53","54","54","55","55","55","56"]
["Standard Accessories","Installation manual","","","","Installation manual","Installation manual"]
["","Operation manual","","","","Operation manual","Operation manual"]
["","Connection pipes","","","","Connection pipes","Connection pipes"]
["Capacity range","HP","","","","8","10","16","18","20","24","26","28","30"]
["Maximum number of connectable indoor units","","","","","36 (5)","36 (5)","36 (5)","36 (5)","36 (5)","36 (5)","36 (5)","36 (5)","36 (5)"]
["Compressor","Type","","","","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor"]
["Weight","Unit","","","kg","137","137"]
["EER","","","","","5.07 (1), 5.03 (2)","4.56 (1), 4.33 (2)","5.07 (1), 5.03 (2)","4.77 (1), 4.62 (2)","4.56 (1), 4.33 (2)","5.07 (1), 5.03 (2)","4.86 (1), 4.74 (2)","4.69 (1), 4.51 (2)","4.56 (1), 4.33 (2)"]
["Refrigerant","Charge","","","TCO2Eq","7.3","8.8"]
["","GWP","","","","2,087.5","2,087.5"]
["","Charge","","","kg","3.5","4.2"]
["","Type","","","","R-410A","R-410A"]
["System","Outdoor unit module 2","","","","","","RWEYQ8T","RWEYQ10T","RWEYQ10T","RWEYQ8T","RWEYQ8T","RWEYQ10T","RWEYQ10T"]
["","Outdoor unit module 3","","","","","","","","","RWEYQ8T","RWEYQ10T","RWEYQ10T","RWEYQ10T"]
["","Outdoor unit module 1","","","","RWEYQ8T","RWEYQ10T","RWEYQ8T","RWEYQ8T","RWEYQ10T","RWEYQ8T","RWEYQ8T","RWEYQ8T","RWEYQ10T"]
["Power input - 50Hz","Cooling","","Nom.","kW","4.42 (1), 4.45 (2)","6.14 (1), 6.35 (2)","8.8 (1), 8.9 (2)","10.6 (1), 10.8 (2)","12.3 (1), 12.7 (2)","13.3 (1), 13.4 (2)","15.0 (1), 15.3 (2)","16.7 (1), 17.2 (2)","18.4 (1), 19.1 (2)"]
["","Heating","","Nom.","kW","4.21 (3), 4.30 (4)","6.00 (3), 6.20 (4)","8.4 (3), 8.6 (4)","10.2 (3), 10.5 (4)","12.0 (3), 12.4 (4)","12.6 (3), 12.9 (4)","14.4 (3), 14.8 (4)","16.2 (3), 16.7 (4)","18.0 (3), 18.6 (4)"]
["Indoor index connection","Nom.","","","","200","250","400","450","500","600","650","700","750"]
["","Min.","","","","100","125","200","225","250","300","325","350","375"]
["","Max.","","","","260","325","520","585","650","780","845","910","975"]
["Cooling capacity","Nom.","","","kW","22.4 (1), 22.4 (2)","28.0 (1), 27.5 (2)","44.8 (1), 44.8 (2)","50.4 (1), 49.9 (2)","56.0 (1), 55.0 (2)","67.2 (1), 67.2 (2)","72.8 (1), 72.3 (2)","78.4 (1), 77.4 (2)","84.0 (1), 82.5 (2)"]
["Piping connections","Liquid","","OD","mm","9.52","9.52","12.7","15.9","15.9","15.9","19.1","19.1","19.1"]
["","","","Type","","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection"]
["","Total piping length","System","Actual","m","300","300","300","300","300","300","300","300","300"]
["","Gas","","OD","mm","19.10 (9)","22.2 (9)","28.6 (8)","28.6 (8)","28.6 (8)","34.9 (8)","34.9 (8)","34.9 (8)","34.9 (8)"]
["","","","Type","","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection"]
["","Drain","","Outlet","","PS 1/2B internal thread","PS 1/2B internal thread","PS 1/2B internal thread","PS 1/2B internal thread","PS 1/2B internal thread","PS 1/2B internal thread","PS 1/2B internal thread","PS 1/2B internal thread","PS 1/2B internal thread"]
["","Level difference","OU - IU","Outdoor unit in highest position","m","50","50","50","50","50","50","50","50","50"]
["","","","Indoor unit in highest position","m","40","40","40","40","40","40","40","40","40"]
["","","IU - IU","Max.","m","15","15","15","15","15","15","15","15","15"]
["","Discharge gas","","OD","mm","15.9 (10), 19.10 (11)","19.1 (10), 22.10 (11)","22.2 (9), 28.60 (10)","22.2 (9), 28.60 (10)","22.2 (9), 28.60 (10)","28.6 (9), 34.90 (10)","28.6 (9), 34.90 (10)","28.6 (9), 34.90 (10)","28.6 (9), 34.90 (10)"]
["","","","Type","","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection"]
["","Heat insulation","","","","Liquid, Suction gas and HP/LP gas","Liquid, Suction gas and HP/LP gas"]
["","Water","","Inlet","","PT1 1/4B internal thread","PT1 1/4B internal thread"]
["","","","Outlet","","PT1 1/4B internal thread","PT1 1/4B internal thread"]
["COP","","","","","5.94 (3), 5.81 (4)","5.25 (3), 5.08 (4)","5.94 (3), 5.81 (4)","5.53 (3), 5.38 (4)","5.25 (3), 5.08 (4)","5.94 (3), 5.81 (4)","5.65 (3), 5.51 (4)","5.43 (3), 5.27 (4)","5.25 (3), 5.08 (4)"]
["Dimensions","Unit","","Width","mm","780","780"]
["","","","Depth","mm","550","550"]
["","","","Height","mm","1,000","1,000"]
["Heating capacity","Nom.","","","kW","25.0 (3), 25.0 (4)","31.5 (3), 31.5 (4)","50.0 (3), 50.0 (4)","56.5 (3), 56.5 (4)","63.0 (3), 63.0 (4)","75.0 (3), 75.0 (4)","81.5 (3), 81.5 (4)","88.0 (3), 88.0 (4)","94.5 (3), 94.5 (4)"]
["Power supply","Phase","","","","3N~","3N~"]
["","Name","","","","Y1","Y1"]
["","Frequency","","","Hz","50","50"]
["","Voltage","","","V","380-415","380-415"]
["Notes","","","","","(1) - Cooling: Indoor temp. 27°CDB; 19°CWB; inlet water temp.: 30°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 100% water (no glycol)","(1) - Cooling: Indoor temp. 27°CDB; 19°CWB; inlet water temp.: 30°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 100% water (no glycol)","(1) - Cooling: Indoor temp. 27°CDB; 19°CWB; inlet water temp.: 30°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 100% water (no glycol)","(1) - Cooling: Indoor temp. 27°CDB; 19°CWB; inlet water temp.: 30°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 100% water (no glycol)","(1) - Cooling: Indoor temp. 27°CDB; 19°CWB; inlet water temp.: 30°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 100% water (no glycol)","(1) - Cooling: Indoor temp. 27°CDB; 19°CWB; inlet water temp.: 30°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 100% water (no glycol)","(1) - Cooling: Indoor temp. 27°CDB; 19°CWB; inlet water temp.: 30°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 100% water (no glycol)","(1) - Cooling: Indoor temp. 27°CDB; 19°CWB; inlet water temp.: 30°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 100% water (no glycol)","(1) - Cooling: Indoor temp. 27°CDB; 19°CWB; inlet water temp.: 30°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 100% water (no glycol)"]
["","","","","","(2) - Cooling: Indoor temp. 27°CDB; 19°CWB; inlet water temp.: 30°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 30% glycol.","(2) - Cooling: Indoor temp. 27°CDB; 19°CWB; inlet water temp.: 30°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 30% glycol.","(2) - Cooling: Indoor temp. 27°CDB; 19°CWB; inlet water temp.: 30°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 30% glycol.","(2) - Cooling: Indoor temp. 27°CDB; 19°CWB; inlet water temp.: 30°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 30% glycol.","(2) - Cooling: Indoor temp. 27°CDB; 19°CWB; inlet water temp.: 30°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 30% glycol.","(2) - Cooling: Indoor temp. 27°CDB; 19°CWB; inlet water temp.: 30°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 30% glycol.","(2) - Cooling: Indoor temp. 27°CDB; 19°CWB; inlet water temp.: 30°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 30% glycol.","(2) - Cooling: Indoor temp. 27°CDB; 19°CWB; inlet water temp.: 30°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 30% glycol.","(2) - Cooling: Indoor temp. 27°CDB; 19°CWB; inlet water temp.: 30°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 30% glycol."]
["","","","","","(3) - Heating: Indoor temp. 20°CDB; inlet water temp.: 20°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 100% water (no glycol).","(3) - Heating: Indoor temp. 20°CDB; inlet water temp.: 20°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 100% water (no glycol).","(3) - Heating: Indoor temp. 20°CDB; inlet water temp.: 20°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 100% water (no glycol).","(3) - Heating: Indoor temp. 20°CDB; inlet water temp.: 20°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 100% water (no glycol).","(3) - Heating: Indoor temp. 20°CDB; inlet water temp.: 20°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 100% water (no glycol).","(3) - Heating: Indoor temp. 20°CDB; inlet water temp.: 20°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 100% water (no glycol).","(3) - Heating: Indoor temp. 20°CDB; inlet water temp.: 20°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 100% water (no glycol).","(3) - Heating: Indoor temp. 20°CDB; inlet water temp.: 20°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 100% water (no glycol).","(3) - Heating: Indoor temp. 20°CDB; inlet water temp.: 20°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 100% water (no glycol)."]
["","","","","","(4) - Heating: Indoor temp. 20°CDB; inlet water temp.: 20°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 30% glycol.","(4) - Heating: Indoor temp. 20°CDB; inlet water temp.: 20°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 30% glycol.","(4) - Heating: Indoor temp. 20°CDB; inlet water temp.: 20°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 30% glycol.","(4) - Heating: Indoor temp. 20°CDB; inlet water temp.: 20°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 30% glycol.","(4) - Heating: Indoor temp. 20°CDB; inlet water temp.: 20°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 30% glycol.","(4) - Heating: Indoor temp. 20°CDB; inlet water temp.: 20°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 30% glycol.","(4) - Heating: Indoor temp. 20°CDB; inlet water temp.: 20°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 30% glycol.","(4) - Heating: Indoor temp. 20°CDB; inlet water temp.: 20°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 30% glycol.","(4) - Heating: Indoor temp. 20°CDB; inlet water temp.: 20°C; equivalent refrigerant piping: 7,5m; level difference: 0m. Rated values are with 30% glycol."]
["","","","","","(5) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(5) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(5) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(5) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(5) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(5) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(5) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(5) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(5) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)"]
["","","","","","(6) - Operation range extension in case of Glycol is used in combination with fieldsettings (see installation manual).","(6) - Operation range extension in case of Glycol is used in combination with fieldsettings (see installation manual).","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings."]
["","","","","","(7) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(7) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(7) - Sound values are measured in a semi-anechoic room.","(7) - Sound values are measured in a semi-anechoic room.","(7) - Sound values are measured in a semi-anechoic room.","(7) - Sound values are measured in a semi-anechoic room.","(7) - Sound values are measured in a semi-anechoic room.","(7) - Sound values are measured in a semi-anechoic room.","(7) - Sound values are measured in a semi-anechoic room."]
["","","","","","(8) - Sound values are measured in a semi-anechoic room.","(8) - Sound values are measured in a semi-anechoic room.","(8) - In case of heat pump system, gas pipe is not used","(8) - In case of heat pump system, gas pipe is not used","(8) - In case of heat pump system, gas pipe is not used","(8) - In case of heat pump system, gas pipe is not used","(8) - In case of heat pump system, gas pipe is not used","(8) - In case of heat pump system, gas pipe is not used","(8) - In case of heat pump system, gas pipe is not used"]
["","","","","","(9) - In case of heat recovery system","(9) - In case of heat pump system, gas pipe is not used","(9) - In case of heat recovery system","(9) - In case of heat recovery system","(9) - In case of heat recovery system","(9) - In case of heat recovery system","(9) - In case of heat recovery system","(9) - In case of heat recovery system","(9) - In case of heat recovery system"]
["","","","","","(10) - In case of heat pump system","(10) - In case of heat recovery system","(10) - In case of heat pump system","(10) - In case of heat pump system","(10) - In case of heat pump system","(10) - In case of heat pump system","(10) - In case of heat pump system","(10) - In case of heat pump system","(10) - In case of heat pump system"]
["","","","","","(11) - This unit should not be installed outdoors, but indoors e.g. in a machine room.","(11) - In case of heat pump system","(11) - This unit should not be installed outdoors, but indoors e.g. in a machine room.","(11) - This unit should not be installed outdoors, but indoors e.g. in a machine room.","(11) - This unit should not be installed outdoors, but indoors e.g. in a machine room.","(11) - This unit should not be installed outdoors, but indoors e.g. in a machine room.","(11) - This unit should not be installed outdoors, but indoors e.g. in a machine room.","(11) - This unit should not be installed outdoors, but indoors e.g. in a machine room.","(11) - This unit should not be installed outdoors, but indoors e.g. in a machine room."]
["","","","","","(12) - Hold ambient temperature at 0-40°C and humidity at 80%RH or less. Heat rejection from the casing: 0.64kW/8HP","(12) - This unit should not be installed outdoors, but indoors e.g. in a machine room.","(12) - Hold ambient temperature at 0-40°C and humidity at 80%RH or less. Heat rejection from the casing: 0.64kW/8HP","(12) - Hold ambient temperature at 0-40°C and humidity at 80%RH or less. Heat rejection from the casing: 0.64kW/8HP","(12) - Hold ambient temperature at 0-40°C and humidity at 80%RH or less. Heat rejection from the casing: 0.64kW/8HP","(12) - Hold ambient temperature at 0-40°C and humidity at 80%RH or less. Heat rejection from the casing: 0.64kW/8HP","(12) - Hold ambient temperature at 0-40°C and humidity at 80%RH or less. Heat rejection from the casing: 0.64kW/8HP","(12) - Hold ambient temperature at 0-40°C and humidity at 80%RH or less. Heat rejection from the casing: 0.64kW/8HP","(12) - Hold ambient temperature at 0-40°C and humidity at 80%RH or less. Heat rejection from the casing: 0.64kW/8HP"]
["","","","","","(13) - Hold ambient temperature at 0-40°C and humidity at 80%RH or less. Heat rejection from the casing: 0.71kW/10HP","(13) - Hold ambient temperature at 0-40°C and humidity at 80%RH or less. Heat rejection from the casing: 0.64kW/8HP","(13) - Hold ambient temperature at 0-40°C and humidity at 80%RH or less. Heat rejection from the casing: 0.71kW/10HP","(13) - Hold ambient temperature at 0-40°C and humidity at 80%RH or less. Heat rejection from the casing: 0.71kW/10HP","(13) - Hold ambient temperature at 0-40°C and humidity at 80%RH or less. Heat rejection from the casing: 0.71kW/10HP","(13) - Hold ambient temperature at 0-40°C and humidity at 80%RH or less. Heat rejection from the casing: 0.71kW/10HP","(13) - Hold ambient temperature at 0-40°C and humidity at 80%RH or less. Heat rejection from the casing: 0.71kW/10HP","(13) - Hold ambient temperature at 0-40°C and humidity at 80%RH or less. Heat rejection from the casing: 0.71kW/10HP","(13) - Hold ambient temperature at 0-40°C and humidity at 80%RH or less. Heat rejection from the casing: 0.71kW/10HP"]
["","","","","","(14) - Refer to refrigerant pipe selection or installation manual","(14) - Hold ambient temperature at 0-40°C and humidity at 80%RH or less. Heat rejection from the casing: 0.71kW/10HP","(14) - Refer to refrigerant pipe selection or installation manual","(14) - Refer to refrigerant pipe selection or installation manual","(14) - Refer to refrigerant pipe selection or installation manual","(14) - Refer to refrigerant pipe selection or installation manual","(14) - Refer to refrigerant pipe selection or installation manual","(14) - Refer to refrigerant pipe selection or installation manual","(14) - Refer to refrigerant pipe selection or installation manual"]
["","","","","","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(15) - Refer to refrigerant pipe selection or installation manual","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C"]
["","","","","","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(16) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current."]
["","","","","","(17) - Contains fluorinated greenhouse gases","(17) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(17) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(17) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(17) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(17) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(17) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(17) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(17) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current."]
["","","","","","(18) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(18) - Contains fluorinated greenhouse gases","(18) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(18) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(18) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(18) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(18) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(18) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(18) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","","(19) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(19) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(19) - TOCA means the total value of each OC set.","(19) - TOCA means the total value of each OC set.","(19) - TOCA means the total value of each OC set.","(19) - TOCA means the total value of each OC set.","(19) - TOCA means the total value of each OC set.","(19) - TOCA means the total value of each OC set.","(19) - TOCA means the total value of each OC set."]
["","","","","","(20) - TOCA means the total value of each OC set.","(20) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(20) - Maximum allowable voltage range variation between phases is 2%.","(20) - Maximum allowable voltage range variation between phases is 2%.","(20) - Maximum allowable voltage range variation between phases is 2%.","(20) - Maximum allowable voltage range variation between phases is 2%.","(20) - Maximum allowable voltage range variation between phases is 2%.","(20) - Maximum allowable voltage range variation between phases is 2%.","(20) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(21) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(21) - TOCA means the total value of each OC set.","(21) - In accordance with EN/IEC 61000-3-11, respectively EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply with Zsys ≤ Zmax, respectively Ssc ≥ minimum Ssc value.","(21) - In accordance with EN/IEC 61000-3-11, respectively EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply with Zsys ≤ Zmax, respectively Ssc ≥ minimum Ssc value.","(21) - In accordance with EN/IEC 61000-3-11, respectively EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply with Zsys ≤ Zmax, respectively Ssc ≥ minimum Ssc value.","(21) - In accordance with EN/IEC 61000-3-11, respectively EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply with Zsys ≤ Zmax, respectively Ssc ≥ minimum Ssc value.","(21) - In accordance with EN/IEC 61000-3-11, respectively EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply with Zsys ≤ Zmax, respectively Ssc ≥ minimum Ssc value.","(21) - In accordance with EN/IEC 61000-3-11, respectively EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply with Zsys ≤ Zmax, respectively Ssc ≥ minimum Ssc value.","(21) - In accordance with EN/IEC 61000-3-11, respectively EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply with Zsys ≤ Zmax, respectively Ssc ≥ minimum Ssc value."]
["","","","","","(22) - Maximum allowable voltage range variation between phases is 2%.","(22) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(22) - EN/IEC 61000-3-11: European/international technical standard setting the limits for voltage changes, voltage fluctuations and flicker in public low-voltage supply systems for equipment with rated ≤ 75A","(22) - EN/IEC 61000-3-11: European/international technical standard setting the limits for voltage changes, voltage fluctuations and flicker in public low-voltage supply systems for equipment with rated ≤ 75A","(22) - EN/IEC 61000-3-11: European/international technical standard setting the limits for voltage changes, voltage fluctuations and flicker in public low-voltage supply systems for equipment with rated ≤ 75A","(22) - EN/IEC 61000-3-11: European/international technical standard setting the limits for voltage changes, voltage fluctuations and flicker in public low-voltage supply systems for equipment with rated ≤ 75A","(22) - EN/IEC 61000-3-11: European/international technical standard setting the limits for voltage changes, voltage fluctuations and flicker in public low-voltage supply systems for equipment with rated ≤ 75A","(22) - EN/IEC 61000-3-11: European/international technical standard setting the limits for voltage changes, voltage fluctuations and flicker in public low-voltage supply systems for equipment with rated ≤ 75A","(22) - EN/IEC 61000-3-11: European/international technical standard setting the limits for voltage changes, voltage fluctuations and flicker in public low-voltage supply systems for equipment with rated ≤ 75A"]
["","","","","","(23) - In accordance with EN/IEC 61000-3-11, respectively EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply with Zsys ≤ Zmax, respectively Ssc ≥ minimum Ssc value.","(23) - Maximum allowable voltage range variation between phases is 2%.","(23) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(23) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(23) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(23) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(23) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(23) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(23) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase"]
["","","","","","(24) - EN/IEC 61000-3-11: European/international technical standard setting the limits for voltage changes, voltage fluctuations and flicker in public low-voltage supply systems for equipment with rated ≤ 75A","(24) - In accordance with EN/IEC 61000-3-11, respectively EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply with Zsys ≤ Zmax, respectively Ssc ≥ minimum Ssc value.","(24) - Ssc: Short-circuit power","(24) - Ssc: Short-circuit power","(24) - Ssc: Short-circuit power","(24) - Ssc: Short-circuit power","(24) - Ssc: Short-circuit power","(24) - Ssc: Short-circuit power","(24) - Ssc: Short-circuit power"]
["","","","","","(25) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(25) - EN/IEC 61000-3-11: European/international technical standard setting the limits for voltage changes, voltage fluctuations and flicker in public low-voltage supply systems for equipment with rated ≤ 75A","(25) - system impedance","(25) - system impedance","(25) - system impedance","(25) - system impedance","(25) - system impedance","(25) - system impedance","(25) - system impedance"]
["","","","","","(26) - Ssc: Short-circuit power","(26) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(26) - Multi combination (16-30HP) data is corresponding with the standard multi combination as mentioned on 3D084911","(26) - Multi combination (16-30HP) data is corresponding with the standard multi combination as mentioned on 3D084911","(26) - Multi combination (16-30HP) data is corresponding with the standard multi combination as mentioned on 3D084911","(26) - Multi combination (16-30HP) data is corresponding with the standard multi combination as mentioned on 3D084911","(26) - Multi combination (16-30HP) data is corresponding with the standard multi combination as mentioned on 3D084911","(26) - Multi combination (16-30HP) data is corresponding with the standard multi combination as mentioned on 3D084911","(26) - Multi combination (16-30HP) data is corresponding with the standard multi combination as mentioned on 3D084911"]
["","","","","","(27) - system impedance","(27) - Ssc: Short-circuit power","(27) - For more details on standard accessories refer to Installation/operation manual","(27) - For more details on standard accessories refer to Installation/operation manual","(27) - For more details on standard accessories refer to Installation/operation manual","(27) - For more details on standard accessories refer to Installation/operation manual","(27) - For more details on standard accessories refer to Installation/operation manual","(27) - For more details on standard accessories refer to Installation/operation manual","(27) - For more details on standard accessories refer to Installation/operation manual"]
["","","","","","(28) - Multi combination (16-30HP) data is corresponding with the standard multi combination as mentioned on 3D084911","(28) - system impedance"]
["","","","","","(29) - For more details on standard accessories refer to Installation/operation manual","(29) - Multi combination (16-30HP) data is corresponding with the standard multi combination as mentioned on 3D084911"]
["","","","","","","(30) - For more details on standard accessories refer to Installation/operation manual"]