{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":26,"n_cols":11,"rows_kept":26,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXC-E"]
[]
[]
[]
[]
["","","","","","RXC20EV1B","RXC25EV1B","RXC35EV1B","RXC50EV1B","RXC60EV1B","RXC71EV1B"]
["Dimensions","Unit","","Height","mm","550","550","550","615","615","695"]
["","","","Width","mm","658","658","658","845","845","930"]
["","","","Depth","mm","273","273","273","300","300","350"]
["Weight","Unit","","","kg","24","24","26","39","39","45"]
["Compressor","Type","","","","Hermetic swing","Hermetic swing","Hermetic swing","Hermetic swing","Hermetic swing","Hermetic swing"]
["Operation range","Cooling","Ambient","Min.","°CDB","10","10","10","-10","-10","-10"]
["","","","Max.","°CDB","46","46","46","46","46","46"]
["","Heating","Ambient","Min.","°CWB","-15","-15","-15","-15","-15","-15"]
["","","","Max.","°CWB","18","18","18","18","18","18"]
["Sound pressure level","Cooling","","High","dBA","45","45","46","51","54","54"]
["Refrigerant","Type","","","","R-32","R-32","R-32","R-32","R-32","R-32"]
["","Charge","","","kg","0.55","0.55","0.75","1","1.1","1.15"]
["","Charge","","","tCO2Eq","0.371","0.371","0.506","0.675","0.743","0.776"]
["","GWP","","","","675","675","675","675","675","675"]
["Piping connections","Piping length","OU - IU","Max.","m","20","20","20","30","30","30"]
["","Additional refrigerant charge","","","kg/m","0,017 (for piping length exceeding 7.5m)","0,017 (for piping length exceeding 7.5m)","0,017 (for piping length exceeding 7.5m)","0,017 (for piping length exceeding 7.5m)","0,017 (for piping length exceeding 7.5m)","0,017 (for piping length exceeding 7.5m)"]
["","Level difference","IU - OU","Max.","m","15","15","15","20","20","20"]
["Power supply","Phase","","","","1~","1~","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50","50","50"]
["","Voltage","","","V","220-440","220-440","220-440","220-440","220-440","220-440"]