{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":114,"n_cols":16,"rows_kept":114,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXYA-A"]
[]
[]
[]
[]
["","","","","","RXYA8A7Y1B","RXYA10A7Y1B","RXYA12A7Y1B","RXYA13A7Y1B","RXYA14A7Y1B","RXYA16A7Y1B","RXYA16A7Y1B.","RXYA18A7Y1B","RXYA18A7Y1B.","RXYA20A7Y1B","RXYA20A7Y1B."]
["System","Outdoor unit module 1","","","","","","","RYMA5A","","","RXYA8A","","RXYA8A","","RXYA8A"]
["","Outdoor unit module 2","","","","","","","RXYA8A","","","RXYA8A","","RXYA10A","","RXYA12A"]
["Recommended combination","","","","","4 x FXFA50A2VEB","4 x FXFA63A2VEB","6 x FXFA50A2VEB","3 x FXFA50A2VEB + 3 x FXFA63A2VEB","1 x FXFA50A2VEB + 5 x FXFA63A2VEB","4 x FXFA63A2VEB + 2 x FXFA80A2VEB","4 x FXFA63A2VEB + 2 x FXFA80A2VEB","3 x FXFA50A2VEB + 5 x FXFA63A2VEB","4 x FXFA50A2VEB + 4 x FXFA63A2VEB","8 x FXFA63A2VEB","10 x FXFA50A2VEB"]
["Recommended combination 2","","","","","4 x FXSA50A2VEB","4 x FXSA63A2VEB","6 x FXSA50A2VEB","3 x FXSA50A2VEB + 3 x FXSA63A2VEB","1 x FXSA50A2VEB + 5 x FXSA63A2VEB","4 x FXSA63A2VEB + 2 x FXSA80A2VEB","4 x FXSA63A2VEB + 2 x FXSA80A2VEB","3 x FXSA50A2VEB + 5 x FXSA63A2VEB","4 x FXSA50A2VEB + 4 x FXSA63A2VEB","8 x FXSA63A2VEB","10 x FXSA50A2VEB"]
["Continuous heating","","","","","","","","Yes","","","Yes","","Yes","","Yes"]
["Cooling capacity","Prated,c","","","kW","22.4 (1)","28","33.5 (1)","36.4","40","45","44.8","50.4 (1)","50.4","56","55.9"]
["Heating capacity","Prated,h","","","kW","22.4 (2)","28","33.5 (2)","36.4","40","45","44.8","50.4 (2)","50.4","56","55.9"]
["","Nom.","","6°CWB","kW","22.4 (2)","28","33.5 (2)","36.4","40","45","44.8","50.4 (2)","50.4","56","55.9"]
["COP at nom. capacity","6°CWB","","","KW/KW","3.83 (2)","3.45 (2)","3.46 (2)","3.76","3.57 (2)","3.52 (2)","3.72","3.66 (2)","3.61","3.37 (2)","3.6"]
["SEER","","","","","7.26","7.06","7.04","7.42","7.63","6.99","7.12","6.87","7.18","6.52","7.16"]
["SEER recommended combination 2","","","","","6.97","6.85","6.62","7.08","7.4","6.88","6.87","6.74","6.85","6.42","6.86"]
["SCOP","","","","","4.11","4.33","4.49","4.11","4.28","4.26","4.35","4.39","4.34","4.14","4.38"]
["SCOP recommended combination 2","","","","","4.1","4.34","4.56","4.19","4.33","4.33","4.38","4.33","4.4","4.11","4.48"]
["Space cooling","A Condition (35°C - 27/19)","","EERd","","3.09","3.06","3.05","3.39","3.11","2.97","3.17","2.52","3.19","2.36","3.12"]
["","","","Pdc","kW","22.4","28","33.5","36.4","40","45","44.8","50.4","50.4","56","55.9"]
["","B Condition (30°C - 27/19)","","EERd","","5.13","4.95","4.49","5.94","4.84","4.65","5.18","5.01","5.18","4.65","4.88"]
["","","","Pdc","kW","16.5","20.6","24.7","26.8","29.5","33.2","33","37.1","37.1","41.3","41.2"]
["","C Condition (25°C - 27/19)","","EERd","","9.12","8.51","8.34","9.04","8.74","8.15","8.63","7.92","8.59","7.2","8.53"]
["","","","Pdc","kW","10.6","13.3","15.9","18","18.9","21.3","21.2","23.9","23.9","26.5","26.5"]
["","D Condition (20°C - 27/19)","","EERd","","15.3","14.8","17.5","13.9","22.5","16.5","14.8","14.8","14.9","16.1","16.3"]
["","","","Pdc","kW","8.13","8.19","8.57","15.5","10.93","11.1","15.9","11.19","16.3","11.79","16.7"]
["Space cooling recommended combination 2","A Condition (35°C - 27/19)","","EERd","","3.02","2.93","2.89","3.27","3.02","2.88","3.05","2.44","3.17","2.28","3.02"]
["","","","Pdc","kW","22.4","28","33.5","36.4","40","45","44.8","50.4","50.4","56","55.9"]
["","B Condition (30°C - 27/19)","","EERd","","4.99","4.82","4.32","5.65","4.78","4.6","4.97","4.41","4.91","4.41","4.68"]
["","","","Pdc","kW","16.5","20.6","24.8","26.8","29.5","33.2","33","37.1","37.1","41.3","41.2"]
["","C Condition (25°C - 27/19)","","EERd","","8.58","8.23","7.64","8.53","8.33","7.98","8.32","7.83","8.11","7.41","8.09"]
["","","","Pdc","kW","10.6","13.3","15.9","17.8","18.9","21.3","21.2","23.9","23.9","26.5","26.5"]
["","D Condition (20°C - 27/19)","","EERd","","14.58","14.4","16.23","13.26","21.53","16.23","14.2","18.25","14.04","15.94","15.5"]
["","","","Pdc","kW","7.82","7.97","8.2","15","10.6","10.8","15.5","10.9","15.8","11.8","16"]
["Space heating (Average climate)","TBivalent","","COPd (declared COP)","","2.8","2.28","2.38","2.74","2.57","2.53","2.87","2.36","2.51","2.23","2.55"]
["","","","Pdh (declared heating cap)","kW","13.7","16","18.4","21.7","20.6","23.2","23.2","27.9","27.9","31","31"]
["","","","Tbiv (bivalent temperature)","°C","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","Space heating (Average climate)-=-E condition (-10°C)","","Space heating (Average climate)-=-E condition (-10°C)-=-COPd (declared COP)","","2.8","2.28","2.38","2.74","2.57","2.53","2.87","2.36","2.51","2.23","2.55"]
["","","","Space heating (Average climate)-=-E condition (-10°C)-=-Pdh (declared heating cap)-=-kW","kW","13.7","16","18.4","21.7","20.6","23.2","23.2","27.9","27.9","31","31"]
["","TOL","","Tol (temperature operating limit)","°C","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","A Condition (-7°C)","","COPd (declared COP)","","3.06","2.67","2.84","3.03","2.94","2.87","3.18","2.7","2.87","2.6","2.95"]
["","","","Pdh (declared heating cap)","kW","12.1","14.2","16.3","19.2","18.2","20.5","20.5","24.7","24.7","27.4","27.4"]
["","B Condition (2°C)","","COPd (declared COP)","","3.81","4.23","4.15","4.02","3.86","3.93","4.17","4.19","4.2","3.84","4.09"]
["","","","Pdh (declared heating cap)","kW","7.38","8.62","9.89","11.7","11.1","12.5","12.5","15","15","16.7","16.7"]
["","C Condition (7°C)","","COPd (declared COP)","","5.27","5.7","6.32","5.11","6.31","6.21","5.45","6.22","5.6","5.92","5.9"]
["","","","Pdh (declared heating cap)","kW","4.76","5.54","6.36","8.4","7.14","8.03","8.05","9.66","9.66","10.7","10.7"]
["","D Condition (12°C)","","COPd (declared COP)","","7.04","7.92","9.14","6.47","6.68","6.04","6.93","6.85","7.49","7.53","8.06"]
["","","","Pdh (declared heating cap)","kW","4.51","5.46","5.52","8.93","5.15","5.07","9.04","6.24","9.97","7.16","10"]
["Space heating (Average climate) recommended combination 2","TBivalent","","COPd (declared COP)","","2.73","2.32","2.38","2.75","2.58","2.54","2.87","2.28","2.27","2.18","2.34"]
["","","","Pdh (declared heating cap)","kW","13.7","16","18.4","21.7","20.6","23.2","23.2","27.9","27.9","31","31"]
["","","","Tbiv (bivalent temperature)","°C","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","TOL","","COPd (declared COP)","","2.73","2.32","2.38","2.75","2.58","2.54","2.87","2.28","2.27","2.18","2.34"]
["","","","Pdh (declared heating cap)","kW","13.7","16","18.4","21.7","20.6","23.2","23.2","27.9","27.9","31","31"]
["","","","Tol (temperature operating limit)","°C","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","A Condition (-7°C)","","COPd (declared COP)","","3","2.62","2.83","3.05","2.95","2.89","3.18","2.62","2.86","2.54","2.96"]
["","","","Pdh (declared heating cap)","kW","12.1","14.2","16.3","19.2","18.2","20.5","20.5","24.7","24.7","27.5","27.4"]
["","B Condition (2°C)","","COPd (declared COP)","","3.8","4.24","4.26","4.12","3.89","3.96","4.18","4.07","4.27","3.79","4.21"]
["","","","Pdh (declared heating cap)","kW","7.45","8.61","9.89","11.7","11.1","12.5","12.5","15","15","16.7","16.7"]
["","C Condition (7°C)","","COPd (declared COP)","","5.35","5.79","6.39","5.24","6.45","6.41","5.57","6.19","5.78","5.98","6.07"]
["","","","Pdh (declared heating cap)","kW","4.76","5.54","6.36","8.54","7.14","8.04","8.08","9.65","9.65","10.7","10.7"]
["","D Condition (12°C)","","COPd (declared COP)","","7.04","7.91","9.39","6.58","6.94","6.47","6.97","8.15","7.59","7.81","8.3"]
["","","","Pdh (declared heating cap)","kW","4.71","5.6","5.8","9.17","5.33","5.36","9.24","7.68","10.3","7.62","10.5"]
["Capacity range","HP","","","","8","10","12","13","14","16","16","18","18","20","20"]
["Maximum number of connectable indoor units","","","","","64 (3)","64 (3)","64 (3)","64","64 (3)","64 (3)","64","64 (3)","64","64 (3)","64"]
["Indoor index connection","Min.","","","","100","125","150","163","175","200","200","225","225","250","250"]
["","Max.","","","","260","325","390","423","455","520","520","585","585","650","650"]
["Dimensions","Unit","","Height","mm","1685","1685","1685","","1685","1685","","1685","","1685"]
["","","","Width","mm","930","930","930","","1240","1240","","1240","","1240"]
["","","","Depth","mm","765","765","765","","765","765","","765","","765"]
["Weight","Unit","","","kg","214","214","214","","297","297","","320","","320"]
["Fan","External static pressure","","Max.","Pa","78","78","78","","78","78","","78","","78"]
["Compressor","Type","","","","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","","Hermetically sealed scroll compressor","","Hermetically sealed scroll compressor"]
["Operation range","Cooling","","Min.","°CDB","-5","-5","-5","","-5","-5","","-5","","-5"]
["","","","Max.","°CDB","46","46","46","","46","46","","46","","46"]
["","Heating","","Min.","°CWB","-20","-20","-20","","-20","-20","","-20","","-20"]
["","","","Max.","°CWB","16","16","16","","16","16","","16","","16"]
["Sound power level","Cooling","","Nom.","dBA","78.3 (5)","78.8 (5)","82.5 (5)","81.3","79.5 (5)","83.7 (5)","81.3","83.4 (5)","81.6","87.9 (5)","83.9"]
["Sound pressure level","Cooling","","Nom.","dBA","56.3 (6)","58","60.8 (6)","59.3","59","61.6 (6)","59.3","63","60.2","67","62.1"]
["Refrigerant","Type","","","","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32"]
["","GWP","","","","675","675","675","675","675","675","675","675","675","675","675"]
["","Charge","","","tCO2Eq","6.08","6.08","6.08","","7.16","7.16","","7.16","","7.16"]
["","Charge","","","kg","9","9","9","","10.6","10.6","","10.6","","10.6"]
["Piping connections","Liquid","","Type","","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection"]
["","","","OD","mm","9.52","9.52","12.7","12.7","12.7","12.7","12.7","12.7","12.7","12.7","12.7"]
["","Gas","","Type","","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection"]
["","","","OD","mm","19.1","19.1","22.2","22.2","22.2","28.6","28.6","28.6","28.6","28.6","28.6"]
["","Equalizing","","OD","mm","","","","19.1","","","19.1","","19.1","","19.1"]
["","Total piping length","System","Actual","m","1000 (7)","1000 (7)","1000 (7)","500","1000 (7)","1000 (7)","500","1000 (7)","500","1000 (7)","500"]
["Standard Accessories","Connection pipes","","","","1","1","1","","1","1","","1","","1"]
["","Installation and operation manual","","","","1","1","1","","1","1","","1","","1"]
["Power supply","Name","","","","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1"]
["","Phase","","","","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m"]
["","","","","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m"]
["","","","","","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system."]
["","","","","","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of"]
["","","","","","(5) - Sound power level is an absolute value that a sound source generates.","(5) - Sound power level is an absolute value that a sound source generates.","(5) - Sound power level is an absolute value that a sound source generates.","(5) - Sound power level is an absolute value that a sound source generates.","(5) - Sound power level is an absolute value that a sound source generates.","(5) - Sound power level is an absolute value that a sound source generates.","(5) - Sound power level is an absolute value that a sound source generates.","(5) - Sound power level is an absolute value that a sound source generates.","(5) - Sound power level is an absolute value that a sound source generates.","(5) - Sound power level is an absolute value that a sound source generates.","(5) - Sound power level is an absolute value that a sound source generates."]
["","","","","","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings."]
["","","","","","(7) - Refer to refrigerant pipe selection or installation manual","(7) - Refer to refrigerant pipe selection or installation manual","(7) - Refer to refrigerant pipe selection or installation manual","(7) - Refer to refrigerant pipe selection or installation manual","(7) - Refer to refrigerant pipe selection or installation manual","(7) - Refer to refrigerant pipe selection or installation manual","(7) - Refer to refrigerant pipe selection or installation manual","(7) - Refer to refrigerant pipe selection or installation manual","(7) - Refer to refrigerant pipe selection or installation manual","(7) - Refer to refrigerant pipe selection or installation manual","(7) - Refer to refrigerant pipe selection or installation manual"]
["","","","","","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB"]
["","","","","","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current."]
["","","","","","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value"]
["","","","","","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current."]
["","","","","","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","","(13) - Maximum allowable voltage range variation between phases is 2%.","(13) - Maximum allowable voltage range variation between phases is 2%.","(13) - Maximum allowable voltage range variation between phases is 2%.","(13) - Maximum allowable voltage range variation between phases is 2%.","(13) - Maximum allowable voltage range variation between phases is 2%.","(13) - Maximum allowable voltage range variation between phases is 2%.","(13) - Maximum allowable voltage range variation between phases is 2%.","(13) - Maximum allowable voltage range variation between phases is 2%.","(13) - Maximum allowable voltage range variation between phases is 2%.","(13) - Maximum allowable voltage range variation between phases is 2%.","(13) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(15) - Sound values are measured in a semi-anechoic room.","(15) - Sound values are measured in a semi-anechoic room.","(15) - Sound values are measured in a semi-anechoic room.","(15) - Sound values are measured in a semi-anechoic room.","(15) - Sound values are measured in a semi-anechoic room.","(15) - Sound values are measured in a semi-anechoic room.","(15) - Sound values are measured in a semi-anechoic room.","(15) - Sound values are measured in a semi-anechoic room.","(15) - Sound values are measured in a semi-anechoic room.","(15) - Sound values are measured in a semi-anechoic room.","(15) - Sound values are measured in a semi-anechoic room."]
["","","","","","(16) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(16) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(16) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(16) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(16) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(16) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(16) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(16) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(16) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(16) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(16) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase"]
["","","","","","(17) - Ssc: Short-circuit power","(17) - Ssc: Short-circuit power","(17) - Ssc: Short-circuit power","(17) - Ssc: Short-circuit power","(17) - Ssc: Short-circuit power","(17) - Ssc: Short-circuit power","(17) - Ssc: Short-circuit power","(17) - Ssc: Short-circuit power","(17) - Ssc: Short-circuit power","(17) - Ssc: Short-circuit power","(17) - Ssc: Short-circuit power"]
["","","","","","(18) - For detailed contents of standard accessories, see installation/operation manual","(18) - For detailed contents of standard accessories, see installation/operation manual","(18) - For detailed contents of standard accessories, see installation/operation manual","(18) - For detailed contents of standard accessories, see installation/operation manual","(18) - For detailed contents of standard accessories, see installation/operation manual","(18) - For detailed contents of standard accessories, see installation/operation manual","(18) - For detailed contents of standard accessories, see installation/operation manual","(18) - For detailed contents of standard accessories, see installation/operation manual","(18) - For detailed contents of standard accessories, see installation/operation manual","(18) - For detailed contents of standard accessories, see installation/operation manual","(18) - For detailed contents of standard accessories, see installation/operation manual"]
["","","","","","(19) - Multi combination (10~20HP) data is corresponding with the standard multi combination","(19) - Multi combination (10~20HP) data is corresponding with the standard multi combination","(19) - Multi combination (10~20HP) data is corresponding with the standard multi combination","(19) - Multi combination (10~20HP) data is corresponding with the standard multi combination","(19) - Multi combination (10~20HP) data is corresponding with the standard multi combination","(19) - Multi combination (10~20HP) data is corresponding with the standard multi combination","(19) - Multi combination (10~20HP) data is corresponding with the standard multi combination","(19) - Multi combination (10~20HP) data is corresponding with the standard multi combination","(19) - Multi combination (10~20HP) data is corresponding with the standard multi combination","(19) - Multi combination (10~20HP) data is corresponding with the standard multi combination","(19) - Multi combination (10~20HP) data is corresponding with the standard multi combination"]