{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":91,"n_cols":8,"rows_kept":91,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXYQ-T8"]
[]
[]
[]
[]
["","","","","","RXYQ8T7Y1B8","RXYQ24T7Y1B8","RXYQ38T7Y1B8"]
["Sound pressure level","Cooling","","Nom.","dBA","58.0 (5)","65.0 (5)","67.2 (5)"]
["Standard Accessories","Installation manual","","","","1","1","1"]
["","Operation manual","","","","1","1","1"]
["","Connection pipes","","","","1","1","1"]
["Capacity range","HP","","","","8","24","38"]
["Operation range","Cooling","","Max.","°CDB","43.0"]
["","","","Min.","°CDB","-5.0"]
["","Heating","","Min.","°CWB","-20.0"]
["","","","Max.","°CWB","15.5"]
["Maximum number of connectable indoor units","","","","","64 (3)","64 (3)","64 (3)"]
["Space cooling","B Condition (30°C - 27/19)","","Pdc","kW","16.5","49.7","75.5"]
["","","","EERd","","4.1","4.0","3.9"]
["","D Condition (20°C - 27/19)","","Pdc","kW","4.8","14.3","21.6"]
["","","","EERd","","8.7","9.5","10.0"]
["","A Condition (35°C - 27/19)","","EERd","","2.5","2.2","2.2"]
["","","","Pdc","kW","22.4","67.4","102.4"]
["","C Condition (25°C - 27/19)","","EERd","","6.4","6.7","6.6"]
["","","","Pdc","kW","10.6","31.9","48.5"]
["SCOP","","","","","3.6","3.7","3.7"]
["Compressor","Type","","","","Hermetically sealed scroll compressor"]
["Weight","Unit","","","kg","187"]
["Refrigerant","Charge","","","TCO2Eq","12.3"]
["","GWP","","","","2,087.5","2,087.5","2,087.5"]
["","Charge","","","kg","5.9"]
["","Type","","","","R-410A","R-410A","R-410A"]
["System","Outdoor unit module 2","","","","","RXYQ16T","RXYQ10T"]
["","Outdoor unit module 3","","","","","","RXYQ20T"]
["","Outdoor unit module 1","","","","","RXYQ8T","RXYQ8T"]
["Indoor index connection","Min.","","","","100.0","300.0","475.0"]
["","Max.","","","","260.0","780.0","1,235.0"]
["Cooling capacity","Prated,c","","","kW","22.4 (1)","67.4 (1)","102.4 (1)"]
["Recommended combination","","","","","4 x FXMQ50P7VEB","4 x FXMQ50P7VEB + 4 x FXMQ63P7VEB + 2 x FXMQ80P7VEB","6 x FXMQ50P7VEB + 10 x FXMQ63P7VEB"]
["Space heating (Average climate)","TOL","","COPd (declared COP)","","2.0","1.8","2.1"]
["","","","Pdh (declared heating cap)","kW","13.7","36.9","58.2"]
["","","","Tol (temperature operating limit)","°C","-10","-10","-10"]
["","D Condition (12°C)","","Pdh (declared heating cap)","kW","6.6","6.6","9.0"]
["","","","COPd (declared COP)","","8.4","8.4","6.7"]
["","B Condition (2°C)","","COPd (declared COP)","","3.1","3.2","3.4"]
["","","","Pdh (declared heating cap)","kW","7.4","19.8","31.3"]
["","C Condition (7°C)","","COPd (declared COP)","","6.4","6.0","5.4"]
["","","","Pdh (declared heating cap)","kW","5.7","12.8","20.1"]
["","A Condition (-7°C)","","COPd (declared COP)","","2.3","2.2","2.4"]
["","","","Pdh (declared heating cap)","kW","12.1","32.6","51.5"]
["","TBivalent","","Pdh (declared heating cap)","kW","13.7","36.9","58.2"]
["","","","Tbiv (bivalent temperature)","°C","-10","-10","-10"]
["","","","COPd (declared COP)","","2.0","1.8","2.1"]
["Piping connections","Liquid","","OD","mm","9.52","15.9","19.1"]
["","","","Type","","Braze connection","Braze connection","Braze connection"]
["","Total piping length","System","Actual","m","1,000 (6)","1,000 (6)","1,000 (6)"]
["","Gas","","OD","mm","19.1","34.9","41.3"]
["","","","Type","","Braze connection","Braze connection","Braze connection"]
["SEER","","","","","5.4","5.5","5.4"]
["Sound power level","Cooling","","Nom.","dBA","78.0 (4)","86.6 (4)","88.9 (4)"]
["Dimensions","Unit","","Width","mm","930"]
["","","","Depth","mm","765"]
["","","","Height","mm","1,685"]
["Fan","External static pressure","","Max.","Pa","78"]
["Heating capacity","Prated,h","","","kW","13.7","36.9","58.2"]
["Power supply","Phase","","","","3N~","3N~","3N~"]
["","Name","","","","Y1","Y1","Y1"]
["","Frequency","","","Hz","50","50","50"]
["","Voltage","","","V","380-415","380-415","380-415"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m"]
["","","","","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m"]
["","","","","","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)"]
["","","","","","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates."]
["","","","","","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings."]
["","","","","","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual"]
["","","","","","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB"]
["","","","","","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current."]
["","","","","","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value"]
["","","","","","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current."]
["","","","","","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set."]
["","","","","","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan"]
["","","","","","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )"]
["","","","","","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality"]
["","","","","","(18) - Sound values are measured in a semi-anechoic room.","(18) - Sound values are measured in a semi-anechoic room.","(18) - Sound values are measured in a semi-anechoic room."]
["","","","","","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA"]
["","","","","","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase"]
["","","","","","(21) - Ssc: Short-circuit power","(21) - Ssc: Short-circuit power","(21) - Ssc: Short-circuit power"]
["","","","","","(22) - For detailed contents of standard accessories, see installation/operation manual","(22) - For detailed contents of standard accessories, see installation/operation manual","(22) - For detailed contents of standard accessories, see installation/operation manual"]
["","","","","","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination"]