{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":85,"n_cols":8,"rows_kept":85,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXYSA-AV1"]
[]
[]
[]
[]
["","","","","","RXYSA4A7V1B","RXYSA5A7V1B","RXYSA6A7V1B"]
["Recommended combination","","","","","3 x FXSA25A2VEB + 1 x FXSA32A2VEB","4 x FXSA32A2VEB","2 x FXSA32A2VEB + 2 x FXSA40A2VEB"]
["Heating capacity","Nom.","","6°CWB","kW","12.1 (2)","14.0 (2)","15.5 (2)"]
["COP at nom. capacity","6°CWB","","","kW/kW","4.49","4.20","4.10"]
["SCOP","","","","","5.1","4.7","4.7"]
["SEER","","","","","8.2","7.7","7.6"]
["Space cooling","A Condition (35°C - 27/19)","","EERd","","3.4","3.1","3.0"]
["","","","Pdc","kW","12.1","14.0","15.5"]
["","B Condition (30°C - 27/19)","","EERd","","5.8","5.3","5.0"]
["","","","Pdc","kW","8.9","10.3","11.4"]
["","C Condition (25°C - 27/19)","","EERd","","10.9","9.8","9.8"]
["","","","Pdc","kW","5.7","6.6","7.3"]
["","D Condition (20°C - 27/19)","","EERd","","18.5","19.4","19.0"]
["","","","Pdc","kW","4.9","4.5","4.9"]
["Space heating (Average climate)","TBivalent","","COPd (declared COP)","","2.8","2.6","2.5"]
["","","","Pdh (declared heating cap)","kW","8.4","9.7","10.7"]
["","","","Tbiv (bivalent temperature)","°C","-10","-10","-10"]
["","TOL","","COPd (declared COP)","","2.8","2.6","2.5"]
["","","","Pdh (declared heating cap)","kW","8.4","9.7","10.7"]
["","","","Tol (temperature operating limit)","°C","-10","-10","-10"]
["","A Condition (-7°C)","","COPd (declared COP)","","3.4","2.9","2.9"]
["","","","Pdh (declared heating cap)","kW","7.4","8.5","9.5"]
["","B Condition (2°C)","","COPd (declared COP)","","4.9","4.5","4.3"]
["","","","Pdh (declared heating cap)","kW","4.5","5.2","5.8"]
["","C Condition (7°C)","","COPd (declared COP)","","7.0","6.7","7.0"]
["","","","Pdh (declared heating cap)","kW","3.3","3.3","3.7"]
["","D Condition (12°C)","","COPd (declared COP)","","8.9","8.9","9.0"]
["","","","Pdh (declared heating cap)","kW","3.9","3.9","3.9"]
["Capacity range","HP","","","","4","5","6"]
["Maximum number of connectable indoor units","","","","","13 (3)","16 (3)","18 (3)"]
["Indoor index connection","Min.","","","","50.0","62.5","70.0"]
["","Nom.","","","","100","125","140"]
["","Max.","","","","130.0","162.5","182.0"]
["Dimensions","Unit","","Height","mm","869","869","869"]
["","","","Width","mm","1,100","1,100","1,100"]
["","","","Depth","mm","460","460","460"]
["Weight","Unit","","","kg","102","102","102"]
["Fan","External static pressure","","Max.","Pa","45","45","45"]
["Compressor","Type","","","","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor"]
["Operation range","Cooling","","Min.","°CDB","-5","-5","-5"]
["","","","Max.","°CDB","46","46","46"]
["","Heating","","Min.","°CWB","-20","-20","-20"]
["","","","Max.","°CWB","16","16","16"]
["Sound power level","Cooling","","Nom.","dBA","67.0 (4)","68.1 (4)","69.0 (4)"]
["Sound pressure level","Cooling","","Nom.","dBA","49.0 (6)","51.0 (6)","51.0 (6)"]
["Refrigerant","Type","","","","R-32","R-32","R-32"]
["","GWP","","","","675.0","675.0","675.0"]
["","Charge","","","kg","3.40","3.40","3.40"]
["Piping connections","Liquid","","Type","","Braze connection","Braze connection","Braze connection"]
["","","","OD","mm","9.52","9.52","9.52"]
["","Gas","","Type","","Braze connection","Braze connection","Braze connection"]
["","","","OD","mm","15.9","15.9","15.9"]
["","Total piping length","System","Actual","m","300 (7)","300 (7)","300 (7)"]
["","Level difference","OU - IU","Outdoor unit in highest position","m","50","50","50"]
["","","","Indoor unit in highest position","m","40","40","40"]
["Standard Accessories","Installation and operation manual","","","","1","1","1"]
["","General safety precautions","","","","1","1","1"]
["","Peel off F-gas label","","","","1","1","1"]
["","Refrigerant label for F-gas regulation","","","","1","1","1"]
["","Tie-wraps","","","","2","2","2"]
["","Auxiliary piping set","","","","1","1","1"]
["","Caution label","","","","1","1","1"]
["Power supply","Name","","","","V1","V1","V1"]
["","Phase","","","","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50"]
["","Voltage","","","V","220-240","220-240","220-240"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m"]
["","","","","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m"]
["","","","","","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system."]
["","","","","","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates."]
["","","","","","(5) - According to ENER Lot 21","(5) - According to ENER Lot 21","(5) - According to ENER Lot 21"]
["","","","","","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings."]
["","","","","","(7) - Refer to refrigerant pipe selection or installation manual","(7) - Refer to refrigerant pipe selection or installation manual","(7) - Refer to refrigerant pipe selection or installation manual"]
["","","","","","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB"]
["","","","","","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current."]
["","","","","","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value"]
["","","","","","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current."]
["","","","","","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","","(13) - TOCA means the total value of each OC set.","(13) - TOCA means the total value of each OC set.","(13) - TOCA means the total value of each OC set."]
["","","","","","(14) - FLA means the nominal running current of the fan","(14) - FLA means the nominal running current of the fan","(14) - FLA means the nominal running current of the fan"]