{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":52,"n_cols":5,"rows_kept":52,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXYSQ-T7Y1B9"]
[]
[]
[]
[]
["","","","","RXYSQ6T7Y1B9"]
["Sound pressure level","Cooling","Nom.","dBA","51 (5)"]
["Standard Accessories","Installation manual","","","Installation manual"]
["","Operation manual","","","Operation manual"]
["","Connection pipes","","","Connection pipes"]
["Capacity range","HP","","","6"]
["Operation range","Cooling","Max.","°CDB","46"]
["","","Min.","°CDB","-5"]
["","Heating","Min.","°CWB","-20"]
["","","Max.","°CWB","15.5"]
["Maximum number of connectable indoor units","","","","64 (3)"]
["Compressor","Type","","","Hermetically sealed swing compressor"]
["Weight","Unit","","kg","104"]
["Refrigerant","Charge","","TCO2Eq","7.5"]
["","GWP","","","2,087.5"]
["","Charge","","kg","3.6"]
["","Type","","","R-410A"]
["Indoor index connection","Min.","","","80"]
["","Max.","","","176"]
["Piping connections","Liquid","OD","mm","9.52"]
["","","Type","","Flare connection"]
["","Gas","OD","mm","19.1"]
["","","Type","","Braze connection"]
["","Heat insulation","","","Both liquid and gas pipes"]
["Sound power level","Cooling","Nom.","dBA","70 (4)"]
["Dimensions","Unit","Width","mm","900"]
["","","Depth","mm","320"]
["","","Height","mm","1,345"]
["Power supply","Phase","","","3N~"]
["","Name","","","Y1"]
["","Frequency","","Hz","50"]
["","Voltage","","V","380-415"]
["Notes","","","","(1) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m. Data for standard efficiency series. Eurovent 2015 tolerances are used."]
["","","","","(2) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m. Data for standard efficiency series. Eurovent 2015 tolerances are used."]
["","","","","(3) - Actual number of units depends on the indoor unit type (VRV DX indoor, RA DX indoor, etc.) and the connection ratio restriction for the system (being; 50% ≤ CR ≤130%)."]
["","","","","(4) - Sound power level is an absolute value that a sound source generates."]
["","","","","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings."]
["","","","","(6) - Sound values are measured in a semi-anechoic room."]
["","","","","(7) - For detailed contents of standard accessories, see installation/operation manual"]
["","","","","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB"]
["","","","","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current."]
["","","","","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current."]
["","","","","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","(12) - TOCA means the total value of each OC set."]
["","","","","(13) - FLA: nominal running current fan"]
["","","","","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","(15) - Maximum allowable voltage range variation between phases is 2%."]