{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":84,"n_cols":8,"rows_kept":84,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXYSQ-T8V"]
[]
[]
[]
[]
["","","","","","RXYSQ4T8VB (Archived)","RXYSQ5T8VB (Archived)","RXYSQ6T8VB (Archived)"]
["Sound pressure level","Cooling","","Nom.","dBA","50.0 (5)","51.0 (5)","51.0 (5)"]
["Standard Accessories","Installation manual","","","","1","1","1"]
["","Operation manual","","","","1","1","1"]
["","Connection pipes","","","","1","1","1"]
["Capacity range","HP","","","","4","5","6"]
["Operation range","Cooling","","Max.","°CDB","46.0","46.0","46.0"]
["","","","Min.","°CDB","-5.0","-5.0","-5.0"]
["","Heating","","Min.","°CWB","-20.0","-20.0","-20.0"]
["","","","Max.","°CWB","15.5","15.5","15.5"]
["Maximum number of connectable indoor units","","","","","64 (3)","64 (3)","64 (3)"]
["Space cooling","B Condition (30°C - 27/19)","","Pdc","kW","8.9","10.3","11.4"]
["","","","EERd","","5.3","4.9","4.9"]
["","D Condition (20°C - 27/19)","","Pdc","kW","4.3","4.5","4.6"]
["","","","EERd","","14.0","15.3","16.4"]
["","A Condition (35°C - 27/19)","","EERd","","3.1","2.7","2.7"]
["","","","Pdc","kW","12.1","14.0","15.5"]
["","C Condition (25°C - 27/19)","","EERd","","9.6","9.2","9.5"]
["","","","Pdc","kW","5.7","6.6","7.3"]
["SCOP","","","","","4.4","4.6","4.9"]
["Compressor","Type","","","","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor"]
["Weight","Unit","","","kg","104","104","104"]
["Refrigerant","Charge","","","TCO2Eq","7.5","7.5","7.5"]
["","GWP","","","","2,087.5","2,087.5","2,087.5"]
["","Charge","","","kg","3.6","3.6","3.6"]
["","Type","","","","R-410A","R-410A","R-410A"]
["Indoor index connection","Min.","","","","50.0","62.5","70.0"]
["","Max.","","","","130.0","162.5","182.0"]
["Cooling capacity","Prated,c","","","kW","12.1 (1)","14.0 (1)","15.5 (1)"]
["Recommended combination","","","","","3 x FXSQ25A2VEB + 1 x FXSQ32A2VEB","4 x FXSQ32A2VEB","2 x FXSQ32A2VEB + 2 x FXSQ40A2VEB"]
["Space heating (Average climate)","TOL","","COPd (declared COP)","","2.6","2.6","2.7"]
["","","","Pdh (declared heating cap)","kW","8.0","9.2","10.2"]
["","","","Tol (temperature operating limit)","°C","-10","-10","-10"]
["","D Condition (12°C)","","Pdh (declared heating cap)","kW","4.1","4.1","4.3"]
["","","","COPd (declared COP)","","7.3","7.9","8.5"]
["","B Condition (2°C)","","COPd (declared COP)","","4.3","4.5","4.7"]
["","","","Pdh (declared heating cap)","kW","4.3","5.0","5.5"]
["","C Condition (7°C)","","COPd (declared COP)","","6.0","6.4","6.8"]
["","","","Pdh (declared heating cap)","kW","3.4","3.5","3.6"]
["","A Condition (-7°C)","","COPd (declared COP)","","2.9","3.0","3.1"]
["","","","Pdh (declared heating cap)","kW","7.0","8.1","9.0"]
["","TBivalent","","Pdh (declared heating cap)","kW","8.0","9.2","10.2"]
["","","","Tbiv (bivalent temperature)","°C","-10","-10","-10"]
["","","","COPd (declared COP)","","2.6","2.6","2.7"]
["Piping connections","Liquid","","OD","mm","9.52","9.52","9.52"]
["","","","Type","","Flare connection","Flare connection","Flare connection"]
["","Total piping length","System","Actual","m","300 (6)","300 (6)","300 (6)"]
["","Gas","","OD","mm","15.9","15.9","19.1"]
["","","","Type","","Flare connection","Flare connection","Braze connection"]
["SEER","","","","","7.0","6.8","7.0"]
["Sound power level","Cooling","","Nom.","dBA","68.0 (4)","69.0 (4)","70.0 (4)"]
["Dimensions","Unit","","Width","mm","900","900","900"]
["","","","Depth","mm","320","320","320"]
["","","","Height","mm","1,345","1,345","1,345"]
["Heating capacity","Prated,h","","","kW","8.0","9.2","10.2"]
["Power supply","Phase","","","","1N~","1N~","1N~"]
["","Name","","","","V1","V1","V1"]
["","Frequency","","","Hz","50","50","50"]
["","Voltage","","","V","220-240","220-240","220-240"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m"]
["","","","","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m"]
["","","","","","(3) - Actual number of units depends on the indoor unit type (VRV DX indoor, RA DX indoor, etc.) and the connection ratio restriction for the system (being; 50% ≤ CR ≤130%).","(3) - Actual number of units depends on the indoor unit type (VRV DX indoor, RA DX indoor, etc.) and the connection ratio restriction for the system (being; 50% ≤ CR ≤130%).","(3) - Actual number of units depends on the indoor unit type (VRV DX indoor, RA DX indoor, etc.) and the connection ratio restriction for the system (being; 50% ≤ CR ≤130%)."]
["","","","","","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates."]
["","","","","","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings."]
["","","","","","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual"]
["","","","","","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB"]
["","","","","","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current."]
["","","","","","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current."]
["","","","","","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","","(11) - TOCA means the total value of each OC set.","(11) - TOCA means the total value of each OC set.","(11) - TOCA means the total value of each OC set."]
["","","","","","(12) - FLA means the nominal running current of the fan","(12) - FLA means the nominal running current of the fan","(12) - FLA means the nominal running current of the fan"]
["","","","","","(13) - The automatic ESEER value corresponds with normal VRV IV-S heat pump operation, including the advanced energy saving functionality (variable refrigerant temperature control).","(13) - The automatic ESEER value corresponds with normal VRV IV-S heat pump operation, including the advanced energy saving functionality (variable refrigerant temperature control).","(13) - The automatic ESEER value corresponds with normal VRV IV-S heat pump operation, including the advanced energy saving functionality (variable refrigerant temperature control)."]
["","","","","","(14) - The standard ESEER value corresponds with normal VRV IV-S heat pump operation, not taking into account the advanced energy saving functionality.","(14) - The standard ESEER value corresponds with normal VRV IV-S heat pump operation, not taking into account the advanced energy saving functionality.","(14) - The standard ESEER value corresponds with normal VRV IV-S heat pump operation, not taking into account the advanced energy saving functionality."]
["","","","","","(15) - Sound values are measured in a semi-anechoic room.","(15) - Sound values are measured in a semi-anechoic room.","(15) - Sound values are measured in a semi-anechoic room."]
["","","","","","(16) - Maximum allowable voltage range variation between phases is 2%.","(16) - Maximum allowable voltage range variation between phases is 2%.","(16) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(17) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(17) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(17) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(18) - For detailed contents of standard accessories, see installation/operation manual","(18) - For detailed contents of standard accessories, see installation/operation manual","(18) - For detailed contents of standard accessories, see installation/operation manual"]
["","","","","","(19) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(19) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(19) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase"]
["","","","","","(20) - Ssc: Short-circuit power","(20) - Ssc: Short-circuit power","(20) - Ssc: Short-circuit power"]