{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":114,"n_cols":7,"rows_kept":114,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RYMA-A"]
[]
[]
[]
[]
["","","","","","RYMA5A7Y1B","RXYA10A7Y1B."]
["System","Outdoor unit module 1","","","","","RYMA5A"]
["","Outdoor unit module 2","","","","","RYMA5A"]
["Recommended combination","","","","","","4 x FXFA63A2VEB"]
["Recommended combination 2","","","","","","4 x FXSA63A2VEB"]
["Continuous heating","","","","","","Yes"]
["Cooling capacity","Prated,c","","","kW","14","28"]
["Heating capacity","Prated,h","","","kW","","28"]
["","Nom.","","6°CWB","kW","","28"]
["COP at nom. capacity","6°CWB","","","KW/KW","","3.66"]
["SEER","","","","","","7.55"]
["SEER recommended combination 2","","","","","","7.23"]
["SCOP","","","","","","4.09"]
["SCOP recommended combination 2","","","","","","4.13"]
["Space cooling","A Condition (35°C - 27/19)","","EERd","","","3.68"]
["","","","Pdc","kW","","28"]
["","B Condition (30°C - 27/19)","","EERd","","","7.57"]
["","","","Pdc","kW","","20.6"]
["","C Condition (25°C - 27/19)","","EERd","","","8.99"]
["","","","Pdc","kW","","13.5"]
["","D Condition (20°C - 27/19)","","EERd","","","11.5"]
["","","","Pdc","kW","","14.1"]
["Space cooling recommended combination 2","A Condition (35°C - 27/19)","","EERd","","","3.53"]
["","","","Pdc","kW","","28"]
["","B Condition (30°C - 27/19)","","EERd","","","7.14"]
["","","","Pdc","kW","","20.6"]
["","C Condition (25°C - 27/19)","","EERd","","","8.53"]
["","","","Pdc","kW","","13.4"]
["","D Condition (20°C - 27/19)","","EERd","","","11.19"]
["","","","Pdc","kW","","13.8"]
["Space heating (Average climate)","TBivalent","","COPd (declared COP)","","","2.69"]
["","","","Pdh (declared heating cap)","kW","","16"]
["","","","Tbiv (bivalent temperature)","°C","","-10"]
["","Space heating (Average climate)-=-E condition (-10°C)","","Space heating (Average climate)-=-E condition (-10°C)-=-COPd (declared COP)","","","2.69"]
["","","","Space heating (Average climate)-=-E condition (-10°C)-=-Pdh (declared heating cap)-=-kW","kW","","16"]
["","TOL","","Tol (temperature operating limit)","°C","","-10"]
["","A Condition (-7°C)","","COPd (declared COP)","","","3"]
["","","","Pdh (declared heating cap)","kW","","14.2"]
["","B Condition (2°C)","","COPd (declared COP)","","","4.37"]
["","","","Pdh (declared heating cap)","kW","","8.6"]
["","C Condition (7°C)","","COPd (declared COP)","","","4.7"]
["","","","Pdh (declared heating cap)","kW","","7.17"]
["","D Condition (12°C)","","COPd (declared COP)","","","5.57"]
["","","","Pdh (declared heating cap)","kW","","8.74"]
["Space heating (Average climate) recommended combination 2","TBivalent","","COPd (declared COP)","","","2.7"]
["","","","Pdh (declared heating cap)","kW","","16"]
["","","","Tbiv (bivalent temperature)","°C","","-10"]
["","TOL","","COPd (declared COP)","","","2.7"]
["","","","Pdh (declared heating cap)","kW","","16"]
["","","","Tol (temperature operating limit)","°C","","-10"]
["","A Condition (-7°C)","","COPd (declared COP)","","","3.02"]
["","","","Pdh (declared heating cap)","kW","","14.2"]
["","B Condition (2°C)","","COPd (declared COP)","","","4.42"]
["","","","Pdh (declared heating cap)","kW","","8.64"]
["","C Condition (7°C)","","COPd (declared COP)","","","4.76"]
["","","","Pdh (declared heating cap)","kW","","7.31"]
["","D Condition (12°C)","","COPd (declared COP)","","","5.62"]
["","","","Pdh (declared heating cap)","kW","","8.87"]
["Capacity range","HP","","","","5","10"]
["Maximum number of connectable indoor units","","","","","64 (3)","64"]
["Indoor index connection","Min.","","","","63","125"]
["","Max.","","","","163","325"]
["Dimensions","Unit","","Height","mm","1685"]
["","","","Width","mm","930"]
["","","","Depth","mm","765"]
["Weight","Unit","","","kg","214"]
["Fan","External static pressure","","Max.","Pa","78"]
["Compressor","Type","","","","Hermetically sealed scroll compressor"]
["Operation range","Cooling","","Min.","°CDB","-5"]
["","","","Max.","°CDB","46"]
["","Heating","","Min.","°CWB","-20"]
["","","","Max.","°CWB","16"]
["Sound power level","Cooling","","Nom.","dBA","78.3 (5)","81.3"]
["Sound pressure level","Cooling","","Nom.","dBA","56.3 (6)","59.3"]
["Refrigerant","Type","","","","R-32","R-32"]
["","GWP","","","","675","675"]
["","Charge","","","tCO2Eq","6.08"]
["","Charge","","","kg","9"]
["Piping connections","Liquid","","Type","","Braze connection","Braze connection"]
["","","","OD","mm","9.52","9.5"]
["","Gas","","Type","","Braze connection","Braze connection"]
["","","","OD","mm","19.1","19.1"]
["","Equalizing","","OD","mm","","19.1"]
["","Total piping length","System","Actual","m","","500"]
["Standard Accessories","Connection pipes","","","","1"]
["","Installation and operation manual","","","","1"]
["Power supply","Name","","","","Y1","Y1"]
["","Phase","","","","3N~","3N~"]
["","Frequency","","","Hz","50","50"]
["","Voltage","","","V","380-415","380-415"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m"]
["","","","","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m"]
["","","","","","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system.","(3) - The actual number of units depends on the connection ratio (CR) and the restrictions for the system."]
["","","","","","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of","(4) - Air Flow Rate (AFR) of multi outdoor systems is sum of AFR of the individual systems it consists of"]
["","","","","","(5) - Sound power level is an absolute value that a sound source generates.","(5) - Sound power level is an absolute value that a sound source generates."]
["","","","","","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(6) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings."]
["","","","","","(7) - Refer to refrigerant pipe selection or installation manual","(7) - Refer to refrigerant pipe selection or installation manual"]
["","","","","","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB"]
["","","","","","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current."]
["","","","","","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(10) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value"]
["","","","","","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(11) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current."]
["","","","","","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","","(13) - Maximum allowable voltage range variation between phases is 2%.","(13) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(15) - Sound values are measured in a semi-anechoic room.","(15) - Sound values are measured in a semi-anechoic room."]
["","","","","","(16) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(16) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase"]
["","","","","","(17) - Ssc: Short-circuit power","(17) - Ssc: Short-circuit power"]
["","","","","","(18) - For detailed contents of standard accessories, see installation/operation manual","(18) - For detailed contents of standard accessories, see installation/operation manual"]
["","","","","","(19) - Multi combination (10~20HP) data is corresponding with the standard multi combination","(19) - Multi combination (10~20HP) data is corresponding with the standard multi combination"]