{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":46,"n_cols":8,"rows_kept":46,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","SEHVX-BAW / SERHQ-BAW1"]
[]
[]
[]
[]
["","","","","SEHVX20BAW / SERHQ020BAW1","SEHVX32BAW / SERHQ032BAW1","SEHVX40BAW / SERHQ020BAW1 + SERHQ020BAW1","SEHVX64BAW / SERHQ032BAW1 + SERHQ032BAW1"]
["Refrigerant charge","Per circuit","","kg","","","7.60","9.60"]
["","Refrigerant charge-=-Per circuit-=-TCO2Eq","","TCO2Eq","","","15.9","20.0"]
["Compressor","Type","","","","","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor"]
["","Quantity","","","","","4","6"]
["Air heat exchanger","Type","","","","","Air cooled coil","Air cooled coil"]
["EER","","","","","","2.80","2.48"]
["ESEER","","","","","","4.40","4.05"]
["Refrigerant","GWP","","","","","2,087.5","2,087.5"]
["","Type","","","","","R-410A","R-410A"]
["","Circuits","Quantity","","","","2","2"]
["","Control","","","","","Electronic expansion valve","Electronic expansion valve"]
["Cooling capacity","Nom.","","kW","","","42.3 (1)","63.3 (1)"]
["Water heat exchanger","Water volume","","l","","","6","9"]
["","Type","","","","","Brazed plate","Brazed plate"]
["","Water flow rate","Min.","l/min","","","46","72"]
["Power input","Cooling","Nom.","kW","","","15.1 (1)","25.5 (1)"]
["","Heating","Nom.","kW","","","13.7 (2)","21.4 (2)"]
["Sound power level","Cooling","Nom.","dBA","","","81","83"]
["COP","","","","","","3.03","2.93"]
["Capacity control","Minimum capacity","","%","","","25","25"]
["","Method","","","","","Inverter controlled","Inverter controlled"]
["Fan","External static pressure","Max.","Pa","","","78","78"]
["Heating capacity","Nom.","","kW","","","41.7 (2)","62.7 (2)"]
["Water circuit","Drain valve / fill valve","","","","","Yes","Yes"]
["","Air purge valve","","","","","Yes","Yes"]
["","Shut off valve","","","","","Yes","Yes"]
["","Safety valve","","bar","","","3","3"]
["Power supply","Phase","","","","","3N~","3N~"]
["","Name","","","","","W1","W1"]
["","Frequency","","Hz","","","50","50"]
["","Voltage","","V","","","400","400"]
["Notes","","","","","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C"]
["","","","","","","(2) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(2) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)"]
["","","","","","","(3) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)","(3) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)"]
["","","","","","","(4) - Water can be used above 5°C. Between 0°C and 5°C a 30% glycol solution (propylene or ethylene) has to be used. Between 0°C and -10°C a 40% glycol solution (propylene or ethylene) has to be used (see installation manual and information related to OPZL opti","(4) - Water can be used above 5°C. Between 0°C and 5°C a 30% glycol solution (propylene or ethylene) has to be used. Between 0°C and -10°C a 40% glycol solution (propylene or ethylene) has to be used (see installation manual and information related to OPZL opti"]
["","","","","","","(5) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info.","(5) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info."]
["","","","","","","(6) - Excluding the water volume in the unit. This volume will guarantee suficient defrost energy for all applications, however, this volume can be multiplied by 0,66 if the heating sepoint is ≥ 45° C (eg. Fan coils)","(6) - Excluding the water volume in the unit. This volume will guarantee suficient defrost energy for all applications, however, this volume can be multiplied by 0,66 if the heating sepoint is ≥ 45° C (eg. Fan coils)"]
["","","","","","","(7) - This is PD between inlet & outlet connections of unit. It includes the water side heat exchanger pressure drop.","(7) - This is PD between inlet & outlet connections of unit. It includes the water side heat exchanger pressure drop."]
["","","","","","","(8) - Including piping + PHE; excluding expansion vessel","(8) - Including piping + PHE; excluding expansion vessel"]
["Energy Efficiency Range","","","","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F"]