{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":29,"n_cols":8,"rows_kept":29,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","SERHQ-BAW1"]
[]
[]
[]
[]
["","","","","SERHQ020BAW1 + SERHQ020BAW1","SERHQ020BAW1","SERHQ032BAW1 + SERHQ032BAW1","SERHQ032BAW1"]
["Compressor","Type","","","Hermetically sealed scroll compressor","","Hermetically sealed scroll compressor"]
["","Quantity","","","4","","6"]
["Weight","Unit","","kg","240","","316"]
["Dimensions","Unit","Width","mm","765","","765"]
["","","Depth","mm","930","","1,240"]
["","","Height","mm","1,680","","1,680"]
["Power supply","Phase","","","3N~","","3N~"]
["","Name","","","W1","","W1"]
["","Frequency","","Hz","50","","50"]
["","Voltage","","V","400","","400"]
["Notes","","","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C"]
["","","","","(2) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","","(2) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)"]
["","","","","(3) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)","","(3) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)"]
["","","","","(4) - Water can be used above 5°C. Between 0°C and 5°C a 30% glycol solution (propylene or ethylene) has to be used. Between 0°C and -10°C a 40% glycol solution (propylene or ethylene) has to be used (see installation manual and information related to OPZL opti","","(4) - Water can be used above 5°C. Between 0°C and 5°C a 30% glycol solution (propylene or ethylene) has to be used. Between 0°C and -10°C a 40% glycol solution (propylene or ethylene) has to be used (see installation manual and information related to OPZL opti"]
["","","","","(5) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info.","","(5) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info."]
["","","","","(6) - Excluding the water volume in the unit. This volume will guarantee suficient defrost energy for all applications, however, this volume can be multiplied by 0,66 if the heating sepoint is ≥ 45° C (eg. Fan coils)","","(6) - Excluding the water volume in the unit. This volume will guarantee suficient defrost energy for all applications, however, this volume can be multiplied by 0,66 if the heating sepoint is ≥ 45° C (eg. Fan coils)"]
["","","","","(7) - This is PD between inlet & outlet connections of unit. It includes the water side heat exchanger pressure drop.","","(7) - This is PD between inlet & outlet connections of unit. It includes the water side heat exchanger pressure drop."]
["","","","","(8) - Including piping + PHE; excluding expansion vessel","","(8) - Including piping + PHE; excluding expansion vessel"]
["Dimensions","Unit","Height","mm","","1680","","1680"]
["","","Width","mm","","765","","765"]
["","","Depth","mm","","930","","1240"]
["Weight","Unit","","kg","","240","","316"]
["Power supply","Frequency","","Hz","","50","","50"]