{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":66,"n_cols":14,"rows_kept":66,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","VAM-FC"]
[]
[]
[]
[]
["","","","","","VAM150FCVE","VAM250FCVE","VAM350FCVE","VAM500FCVE","VAM650FCVE","VAM800FCVE","VAM1000FCVE","VAM1500FCVE","VAM2000FCVE"]
["Operation range","Min.","","","°CDB","-15","-15"]
["","Max.","","","°CDB","50","50"]
["","Relative humidity","","","%","80 or less","80 or less"]
["SEC class","","","","","B, See note 4","B, See note 4"]
["Weight","Unit","","","kg","24.0","24.0"]
["Heat exchange system","","","","","Air to air cross flow total heat (sensible + latent heat) exchange","Air to air cross flow total heat (sensible + latent heat) exchange","Air to air cross flow total heat (sensible + latent heat) exchange","Air to air cross flow total heat (sensible + latent heat) exchange","Air to air cross flow total heat (sensible + latent heat) exchange","Air to air cross flow total heat (sensible + latent heat) exchange","Air to air cross flow total heat (sensible + latent heat) exchange","Air to air cross flow total heat (sensible + latent heat) exchange","Air to air cross flow total heat (sensible + latent heat) exchange"]
["Operation mode","","","","","Heat exchange mode, bypass mode, fresh-up mode","Heat exchange mode, bypass mode, fresh-up mode","Heat exchange mode, bypass mode, fresh-up mode","Heat exchange mode, bypass mode, fresh-up mode","Heat exchange mode, bypass mode, fresh-up mode","Heat exchange mode, bypass mode, fresh-up mode","Heat exchange mode, bypass mode, fresh-up mode","Heat exchange mode, bypass mode, fresh-up mode","Heat exchange mode, bypass mode, fresh-up mode"]
["Maximum flow rate at 100 Pa ESP","Flow rate","","","m³/h","130","207"]
["Sound power level (Lwa)","dB","","","","40","43","48","50","51","53","53","55","57"]
["Annual electricity consumption","kWh/a","","","","771 (4)","580 (4)"]
["Power input - 50Hz","Heat exchange mode","Nom.","Ultra high","kW","0.132","0.161"]
["","Bypass mode","Nom.","Ultra high","kW","0.132","0.161"]
["Heat exchange element","","","","","Specially processed non-flammable paper","Specially processed non-flammable paper","Specially processed non-flammable paper","Specially processed non-flammable paper","Specially processed non-flammable paper","Specially processed non-flammable paper","Specially processed non-flammable paper","Specially processed non-flammable paper","Specially processed non-flammable paper"]
["Sound pressure level - 50Hz","Heat exchange mode","","Ultra high","dBA","27.0","28.0"]
["","Bypass mode","","Ultra high","dBA","27.0","28.0"]
["Dimensions","Unit","","Width","mm","776","776"]
["","","","Depth","mm","525","525"]
["","","","Height","mm","285","285"]
["Casing","Material","","","","Galvanised steel plate","Galvanised steel plate"]
["Fan","External static pressure - 50Hz","","Ultra high","Pa","90.0","70.0"]
["","Air flow rate - 50Hz","Heat exchange mode","Ultra high","m³/h","150","250"]
["","","Bypass mode","Ultra high","m³/h","150","250"]
["Annual heating saved","Cold climate","","","kWh/a","8,941 (4)","8,426 (4)"]
["","Average climate","","","kWh/a","4,571 (4)","4,307 (4)"]
["","Warm climate","","","kWh/a","2,067 (4)","1,948 (4)"]
["Connection duct diameter","mm","","","","100","150","150","200","200","250","250","350","350"]
["Power supply","Phase","","","","1~","1~"]
["","Name","","","","VE","VE"]
["","Frequency","","","Hz","50/60","50/60"]
["","Voltage","","","V","220-240/220","220-240/220"]
["Notes","","","","","(1) - Measured on fan curve 15. Refer to fan curves.","(1) - Measured on fan curve 15. Refer to fan curves.","(1) - Measured on fan curve 15. Refer to fan curves.","(1) - Measured on fan curve 15. Refer to fan curves.","(1) - Measured on fan curve 15. Refer to fan curves.","(1) - Measured on fan curve 15. Refer to fan curves.","(1) - Measured on fan curve 15. Refer to fan curves.","(1) - Measured on fan curve 15. Refer to fan curves.","(1) - Measured on fan curve 15. Refer to fan curves."]
["","","","","","(2) - Measured according to JIS B 8628","(2) - Measured according to JIS B 8628","(2) - Measured according to JIS B 8628","(2) - Measured according to JIS B 8628","(2) - Measured according to JIS B 8628","(2) - Measured according to JIS B 8628","(2) - Measured according to JIS B 8628","(2) - Measured according to JIS B 8628","(2) - Measured according to JIS B 8628"]
["","","","","","(3) - Measured at reference flow rate according to EN13141-7","(3) - Measured at reference flow rate according to EN13141-7"]
["","","","","","(4) - In accordance with commission regulation (EU) No 1254/2014","(4) - In accordance with commission regulation (EU) No 1254/2014"]
["","","","","","(5) - In accordance with commission regulation (EU) No 1253/2014","(5) - In accordance with commission regulation (EU) No 1253/2014"]
["","","","","","(6) - At reference flow rate in accordance with commission regulation (EU) No 1254/2014","(6) - At reference flow rate in accordance with commission regulation (EU) No 1254/2014"]
["","","","","","(7) - Clean the filter when the filter icon appears on the controller screen. Regular filter cleaning is important for delivered air quality and for the unit's energy efficiency.","(7) - Clean the filter when the filter icon appears on the controller screen. Regular filter cleaning is important for delivered air quality and for the unit's energy efficiency."]
["","","","","","(8) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(8) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(9) - Maximum allowable voltage range variation between phases is 2%.","(9) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(10) - MCA/MFA: MCA = 1.25 x FLA(FM1) + FLA(FM2); MFA ≤ 4 x FLA; (VAM2000 is regarded as 2x VAM1000)","(10) - MCA/MFA: MCA = 1.25 x FLA(FM1) + FLA(FM2); MFA ≤ 4 x FLA; (VAM2000 is regarded as 2x VAM1000)"]
["","","","","","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA"]
["Power input - 50Hz","Heat exchange mode","Nom.","Ultra high","kW","","","0.071 (1)","0.147 (1)","0.188 (1)","0.320 (1)","0.360 (1)","0.617 (1)","0.685 (1)"]
["","Bypass mode","Nom.","Ultra high","kW","","","0.071 (1)","0.147 (1)","0.188 (1)","0.320 (1)","0.360 (1)","0.617 (1)","0.685 (1)"]
["Casing","Material","","","","","","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate"]
["Dimensions","Unit","","Height","mm","","","301","301","364","364","364","726","726"]
["","","","Width","mm","","","828","828","1000","1000","1000","1510","1510"]
["","","","Depth","mm","","","816","816","868","868","1160","868","1160"]
["Weight","Unit","","","kg","","","33","33","51","54","63","128","145"]
["Fan","Air flow rate - 50Hz","Heat exchange mode","Ultra high","m³/h","","","350 (1)","500 (1)","650 (1)","800 (1)","1000 (1)","1500 (1)","2000 (1)"]
["","","Bypass mode","Ultra high","m³/h","","","350 (1)","500 (1)","650 (1)","800 (1)","1000 (1)","1500 (1)","2000 (1)"]
["","External static pressure - 50Hz","","Ultra high","Pa","","","103 (1)","83.0 (1)","100 (1)","109 (1)","147 (1)","116 (1)","132 (1)"]
["Operation range","Min.","","","°CDB","","","-15","-15","-15","-15","-15","-15","-15"]
["","Max.","","","°CDB","","","50","50","50","50","50","50","50"]
["","Relative humidity","","","%","","","80 or less","80 or less","80 or less","80 or less","80 or less","80 or less","80 or less"]
["Sound pressure level - 50Hz","Heat exchange mode","","Ultra high","dBA","","","32.0","33.0","34.5","36.0","36.0","39.5","40.0"]
["","Bypass mode","","Ultra high","dBA","","","32.0","33.5","34.5","36.0","36.0","40.5","40.0"]
["Power supply","Name","","","","","","VE","VE","VE","VE","VE","VE","VE"]
["","Phase","","","","","","1~","1~","1~","1~","1~","1~","1~"]
["","Frequency","","","Hz","","","50/60","50/60","50/60","50/60","50/60","50/60","50/60"]
["","Voltage","","","V","","","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220"]